## Bldg Info
Measurement Date: | 2010-10-13
Item | Data entry | Notes/ comments
Building: | Phillip J. Bean Medical Center
Address: | 24035 Three Notch Road
Hollywood, MD 20636
GPS coordinates: | 38-19-34.8N
076-33-08.58W
Contact Title:
Contact Name: | Alan A. Buster Jr.
Telephone: | (301) 373-7905
Number of Floors: | 3
Construction type: | Brick/Masonry Block
Approximate Outside dimensions (ft)
Approximate area (sq ft): | 37000
Control Channel Quality:
RCC Test Team Members: | John Tillinghast
Dennis Kelleher

## Photos
Phillip J. Bean Medical Center Front View
Phillip J. Bean Medical Center Front View
Phillip J. Bean Medical Center Front View
Bean Medical Center Aerial View wit Test Transmitter Location Shown

## Floor Plan
FLOOR PLAN NOT AVAILABLE AT TIME OF SURVEY

## RSSI
Site Name: | Phillip J. Bean Medical Center
Calculations |  |  |  | Marker File Locations |  |  |  | Measured Data
Marker Matrix |  | Average RSSI (dBm) |  | Marker # | Calc # of rows | 1st row | last row # |  | Test Tx | Control Chan
Measurement location/route | Markers |  |  | 1 | 286 | 6 | 291 | Frequency: | 868.7875 | 866.4375
|  | Test Tranmsitter | Control Channel | 2 | 197 | 292 | 488 | Marker | RSSI | RSSI
Description |  | 868.7875 MHZ | 866.4375 MHZ | 3 | 19 | 489 | 507 | 1 | -41 | -85
Outside: Along East Wall, then Front | 1 | -44.8671 | -80.1329 | 4 | 52 | 508 | 559 | 1 | -39 | -81
Basement: SW Hall-Elevator to Mail Room to SW Corner | 2 | -88.7919 | -114.1269 | 5 | 125 | 560 | 684 | 1 | -46 | -78
Electrical Room (SE Corner) | 3 | -79 | -102.7895 | 6 | 190 | 685 | 874 | 1 | -45 | -84
Locker Room Hallway - Locker Room to Stairwell | 4 | -89.4808 | -111.3654 | 7 | 212 | 875 | 1086 | 1 | -46 | -78
North Stairwell (Basement to 2nd Floor) | 5 | -73.208 | -97.44 | 8 | 69 | 1087 | 1155 | 1 | -47 | -78
1st Flr: Ultrasound 4 to CT Scan to Film Storage to Nuclear Medicine to Gallery | 6 | -73.1684 | -109.9737 | 9 | 239 | 1156 | 1394 | 1 | -47 | -85
1st Flr: South Stairwell to Exam Rm 5 to Exam Rm 18 to Gallery | 7 | -78.4764 | -104.9245 | 10 | 227 | 1395 | 1621 | 1 | -39 | -79
Elevator (Lobby to 2nd Floor) | 8 | -63.7246 | -96.7101 | 11 | 110 | 1622 | 1731 | 1 | -43 | -81
2nd Flr: South Stairwell to Exam Rm 4 to Endoscopy to Gallery | 9 | -74.8075 | -102.0795 | Total rows | 1726 |  |  | 1 | -48 | -79
2nd Flr: Cysto to Exam Rm 6 to Dr Harvey's Office to Gallery | 10 | -64.6344 | -102.4626 |  |  |  |  | 1 | -38 | -82
South Stairwell (2nd Floor to Basement) | 11 | -64.7091 | -97.4182 |  |  |  |  | 1 | -43 | -77
Average RSSI inside building (dBm): |  | -74.5847 | -104.5771 |  |  |  |  | 1 | -37 | -72
Average building loss (dB): |  | -29.7176 | -24.4442 |  |  |  |  | 1 | -46 | -75
[8 empty] | 1 | -37 | -83
[8 empty] | 1 | -39 | -82
Building Coverage (%) | [7 empty] | 1 | -53 | -74
|  | Tetst TX | Control Ch |  |  |  |  | 1 | -38 | -76
Test points <-105 dBm: |  | 8 | 695 |  |  |  |  | 1 | -38 | -88
Total test points: |  | 1440 | 1440 |  |  |  |  | 1 | -45 | -79
% covered: |  | 99.44% | 51.74% |  |  |  |  | 1 | -41 | -80
[8 empty] | 1 | -52 | -75
[8 empty] | 1 | -50 | -82
[8 empty] | 1 | -51 | -87
[8 empty] | 1 | -43 | -101
[8 empty] | 1 | -45 | -85
[8 empty] | 1 | -38 | -78
[8 empty] | 1 | -40 | -78
[8 empty] | 1 | -44 | -76
[8 empty] | 1 | -49 | -84
[8 empty] | 1 | -44 | -78
[8 empty] | 1 | -42 | -93
[8 empty] | 1 | -46 | -79
[8 empty] | 1 | -47 | -92
[8 empty] | 1 | -44 | -78
[8 empty] | 1 | -44 | -84
[8 empty] | 1 | -46 | -84
[8 empty] | 1 | -45 | -90
[8 empty] | 1 | -42 | -83
[8 empty] | 1 | -51 | -84
[8 empty] | 1 | -41 | -78
[8 empty] | 1 | -37 | -77
[8 empty] | 1 | -38 | -89
[8 empty] | 1 | -38 | -77
[8 empty] | 1 | -42 | -85
[8 empty] | 1 | -33 | -73
[8 empty] | 1 | -35 | -80
[8 empty] | 1 | -41 | -94
[8 empty] | 1 | -43 | -80
[8 empty] | 1 | -46 | -76
[8 empty] | 1 | -42 | -79
[8 empty] | 1 | -40 | -78
[8 empty] | 1 | -44 | -80
[8 empty] | 1 | -49 | -81
[8 empty] | 1 | -43 | -75
[8 empty] | 1 | -51 | -80
[8 empty] | 1 | -42 | -78
[8 empty] | 1 | -47 | -76
[8 empty] | 1 | -40 | -96
[8 empty] | 1 | -43 | -79
[8 empty] | 1 | -43 | -80
[8 empty] | 1 | -49 | -85
[8 empty] | 1 | -40 | -75
[8 empty] | 1 | -42 | -82
[8 empty] | 1 | -37 | -81
[8 empty] | 1 | -41 | -79
[8 empty] | 1 | -41 | -80
[8 empty] | 1 | -42 | -83
[8 empty] | 1 | -36 | -92
[8 empty] | 1 | -51 | -77
[8 empty] | 1 | -39 | -74
[8 empty] | 1 | -49 | -98
[8 empty] | 1 | -50 | -89
[8 empty] | 1 | -46 | -93
[8 empty] | 1 | -49 | -76
[8 empty] | 1 | -50 | -90
[8 empty] | 1 | -47 | -91
[8 empty] | 1 | -43 | -80
[8 empty] | 1 | -38 | -79
[8 empty] | 1 | -43 | -82
[8 empty] | 1 | -38 | -76
[8 empty] | 1 | -48 | -84
[8 empty] | 1 | -38 | -82
[8 empty] | 1 | -33 | -80
[8 empty] | 1 | -36 | -82
[8 empty] | 1 | -37 | -80
[8 empty] | 1 | -38 | -88
[8 empty] | 1 | -38 | -84
[8 empty] | 1 | -36 | -74
[8 empty] | 1 | -49 | -89
[8 empty] | 1 | -39 | -92
[8 empty] | 1 | -40 | -97
[8 empty] | 1 | -62 | -74
[8 empty] | 1 | -39 | -80
[8 empty] | 1 | -43 | -87
[8 empty] | 1 | -37 | -80
[8 empty] | 1 | -33 | -81
[8 empty] | 1 | -40 | -84
[8 empty] | 1 | -39 | -75
[8 empty] | 1 | -38 | -82
[8 empty] | 1 | -36 | -74
[8 empty] | 1 | -36 | -78
[8 empty] | 1 | -34 | -83
[8 empty] | 1 | -36 | -84
[8 empty] | 1 | -36 | -74
[8 empty] | 1 | -48 | -89
[8 empty] | 1 | -35 | -93
[8 empty] | 1 | -38 | -81
[8 empty] | 1 | -37 | -85
[8 empty] | 1 | -41 | -91
[8 empty] | 1 | -37 | -72
[8 empty] | 1 | -38 | -86
[8 empty] | 1 | -38 | -78
[8 empty] | 1 | -38 | -78
[8 empty] | 1 | -46 | -79
[8 empty] | 1 | -42 | -82
[8 empty] | 1 | -45 | -77
[8 empty] | 1 | -42 | -94
[8 empty] | 1 | -37 | -80
[8 empty] | 1 | -42 | -75
[8 empty] | 1 | -36 | -85
[8 empty] | 1 | -41 | -84
[8 empty] | 1 | -41 | -81
[8 empty] | 1 | -40 | -81
[8 empty] | 1 | -30 | -80
[8 empty] | 1 | -36 | -85
[8 empty] | 1 | -38 | -78
[8 empty] | 1 | -40 | -87
[8 empty] | 1 | -37 | -78
[8 empty] | 1 | -38 | -78
[8 empty] | 1 | -41 | -73
[8 empty] | 1 | -41 | -75
[8 empty] | 1 | -50 | -80
[8 empty] | 1 | -41 | -77
[8 empty] | 1 | -38 | -75
[8 empty] | 1 | -37 | -77
[8 empty] | 1 | -38 | -75
[8 empty] | 1 | -44 | -78
[8 empty] | 1 | -37 | -72
[8 empty] | 1 | -50 | -77
[8 empty] | 1 | -38 | -85
[8 empty] | 1 | -38 | -81
[8 empty] | 1 | -45 | -81
[8 empty] | 1 | -42 | -87
[8 empty] | 1 | -47 | -80
[8 empty] | 1 | -41 | -75
[8 empty] | 1 | -42 | -75
[8 empty] | 1 | -48 | -79
[8 empty] | 1 | -40 | -82
[8 empty] | 1 | -44 | -85
[8 empty] | 1 | -45 | -77
[8 empty] | 1 | -40 | -81
[8 empty] | 1 | -41 | -85
[8 empty] | 1 | -34 | -87
[8 empty] | 1 | -46 | -80
[8 empty] | 1 | -52 | -85
[8 empty] | 1 | -56 | -73
[8 empty] | 1 | -48 | -78
[8 empty] | 1 | -40 | -79
[8 empty] | 1 | -46 | -82
[8 empty] | 1 | -51 | -81
[8 empty] | 1 | -44 | -86
[8 empty] | 1 | -37 | -76
[8 empty] | 1 | -38 | -81
[8 empty] | 1 | -40 | -84
[8 empty] | 1 | -42 | -92
[8 empty] | 1 | -39 | -82
[8 empty] | 1 | -42 | -75
[8 empty] | 1 | -39 | -92
[8 empty] | 1 | -41 | -94
[8 empty] | 1 | -36 | -88
[8 empty] | 1 | -37 | -76
[8 empty] | 1 | -41 | -78
[8 empty] | 1 | -45 | -79
[8 empty] | 1 | -42 | -72
[8 empty] | 1 | -42 | -81
[8 empty] | 1 | -36 | -84
[8 empty] | 1 | -42 | -86
[8 empty] | 1 | -39 | -77
[8 empty] | 1 | -43 | -75
[8 empty] | 1 | -41 | -77
[8 empty] | 1 | -42 | -77
[8 empty] | 1 | -42 | -73
[8 empty] | 1 | -42 | -76
[8 empty] | 1 | -44 | -69
[8 empty] | 1 | -44 | -74
[8 empty] | 1 | -42 | -76
[8 empty] | 1 | -58 | -69
[8 empty] | 1 | -48 | -65
[8 empty] | 1 | -50 | -68
[8 empty] | 1 | -41 | -67
[8 empty] | 1 | -43 | -68
[8 empty] | 1 | -49 | -78
[8 empty] | 1 | -53 | -69
[8 empty] | 1 | -46 | -72
[8 empty] | 1 | -48 | -70
[8 empty] | 1 | -48 | -75
[8 empty] | 1 | -47 | -71
[8 empty] | 1 | -40 | -74
[8 empty] | 1 | -40 | -77
[8 empty] | 1 | -52 | -80
[8 empty] | 1 | -50 | -84
[8 empty] | 1 | -40 | -76
[8 empty] | 1 | -44 | -85
[8 empty] | 1 | -48 | -80
[8 empty] | 1 | -45 | -76
[8 empty] | 1 | -54 | -87
[8 empty] | 1 | -62 | -77
[8 empty] | 1 | -47 | -79
[8 empty] | 1 | -48 | -81
[8 empty] | 1 | -39 | -76
[8 empty] | 1 | -54 | -75
[8 empty] | 1 | -71 | -90
[8 empty] | 1 | -52 | -77
[8 empty] | 1 | -54 | -82
[8 empty] | 1 | -42 | -79
[8 empty] | 1 | -47 | -75
[8 empty] | 1 | -44 | -70
[8 empty] | 1 | -45 | -82
[8 empty] | 1 | -55 | -78
[8 empty] | 1 | -50 | -75
[8 empty] | 1 | -46 | -76
[8 empty] | 1 | -45 | -77
[8 empty] | 1 | -43 | -77
[8 empty] | 1 | -40 | -75
[8 empty] | 1 | -45 | -73
[8 empty] | 1 | -44 | -77
[8 empty] | 1 | -43 | -74
[8 empty] | 1 | -53 | -92
[8 empty] | 1 | -40 | -78
[8 empty] | 1 | -42 | -72
[8 empty] | 1 | -50 | -78
[8 empty] | 1 | -48 | -75
[8 empty] | 1 | -55 | -71
[8 empty] | 1 | -43 | -91
[8 empty] | 1 | -48 | -83
[8 empty] | 1 | -47 | -77
[8 empty] | 1 | -48 | -77
[8 empty] | 1 | -47 | -85
[8 empty] | 1 | -52 | -84
[8 empty] | 1 | -48 | -79
[8 empty] | 1 | -42 | -77
[8 empty] | 1 | -57 | -71
[8 empty] | 1 | -53 | -81
[8 empty] | 1 | -44 | -76
[8 empty] | 1 | -61 | -69
[8 empty] | 1 | -51 | -70
[8 empty] | 1 | -46 | -73
[8 empty] | 1 | -44 | -76
[8 empty] | 1 | -47 | -80
[8 empty] | 1 | -43 | -75
[8 empty] | 1 | -58 | -76
[8 empty] | 1 | -49 | -73
[8 empty] | 1 | -47 | -78
[8 empty] | 1 | -47 | -75
[8 empty] | 1 | -48 | -81
[8 empty] | 1 | -51 | -75
[8 empty] | 1 | -53 | -71
[8 empty] | 1 | -51 | -75
[8 empty] | 1 | -50 | -83
[8 empty] | 1 | -46 | -75
[8 empty] | 1 | -51 | -74
[8 empty] | 1 | -46 | -78
[8 empty] | 1 | -45 | -74
[8 empty] | 1 | -62 | -81
[8 empty] | 1 | -45 | -82
[8 empty] | 1 | -63 | -76
[8 empty] | 1 | -51 | -83
[8 empty] | 1 | -63 | -82
[8 empty] | 1 | -51 | -78
[8 empty] | 1 | -60 | -84
[8 empty] | 1 | -77 | -78
[8 empty] | 1 | -75 | -70
[8 empty] | 1 | -47 | -81
[8 empty] | 1 | -55 | -75
[8 empty] | 1 | -48 | -76
[8 empty] | 1 | -60 | -81
[8 empty] | 1 | -74 | -85
[8 empty] | 1 | -44 | -79
[8 empty] | 1 | -46 | -83
[8 empty] | 1 | -52 | -94
[8 empty] | 1 | -52 | -83
[8 empty] | 1 | -51 | -74
[8 empty] | 1 | -53 | -77
[8 empty] | 1 | -81 | -120
[8 empty] | 1 | -78 | -120
[8 empty] | 2 | -80 | -120
[8 empty] | 2 | -80 | -120
[8 empty] | 2 | -97 | -119
[8 empty] | 2 | -96 | -120
[8 empty] | 2 | -81 | -115
[8 empty] | 2 | -80 | -114
[8 empty] | 2 | -86 | -111
[8 empty] | 2 | -81 | -112
[8 empty] | 2 | -79 | -115
[8 empty] | 2 | -78 | -114
[8 empty] | 2 | -80 | -120
[8 empty] | 2 | -77 | -119
[8 empty] | 2 | -81 | -120
[8 empty] | 2 | -91 | -120
[8 empty] | 2 | -93 | -119
[8 empty] | 2 | -89 | -120
[8 empty] | 2 | -89 | -120
[8 empty] | 2 | -109 | -120
[8 empty] | 2 | -91 | -120
[8 empty] | 2 | -103 | -119
[8 empty] | 2 | -95 | -120
[8 empty] | 2 | -92 | -120
[8 empty] | 2 | -96 | -120
[8 empty] | 2 | -86 | -120
[8 empty] | 2 | -90 | -120
[8 empty] | 2 | -103 | -118
[8 empty] | 2 | -91 | -120
[8 empty] | 2 | -91 | -119
[8 empty] | 2 | -106 | -120
[8 empty] | 2 | -85 | -120
[8 empty] | 2 | -92 | -120
[8 empty] | 2 | -91 | -120
[8 empty] | 2 | -96 | -120
[8 empty] | 2 | -92 | -120
[8 empty] | 2 | -89 | -116
[8 empty] | 2 | -97 | -120
[8 empty] | 2 | -93 | -120
[8 empty] | 2 | -94 | -116
[8 empty] | 2 | -112 | -120
[8 empty] | 2 | -95 | -120
[8 empty] | 2 | -92 | -116
[8 empty] | 2 | -88 | -120
[8 empty] | 2 | -97 | -120
[8 empty] | 2 | -93 | -120
[8 empty] | 2 | -91 | -120
[8 empty] | 2 | -95 | -120
[8 empty] | 2 | -97 | -120
[8 empty] | 2 | -98 | -120
[8 empty] | 2 | -97 | -117
[8 empty] | 2 | -103 | -120
[8 empty] | 2 | -100 | -113
[8 empty] | 2 | -93 | -118
[8 empty] | 2 | -88 | -120
[8 empty] | 2 | -89 | -119
[8 empty] | 2 | -84 | -120
[8 empty] | 2 | -88 | -120
[8 empty] | 2 | -100 | -120
[8 empty] | 2 | -92 | -119
[8 empty] | 2 | -92 | -118
[8 empty] | 2 | -93 | -120
[8 empty] | 2 | -93 | -120
[8 empty] | 2 | -86 | -120
[8 empty] | 2 | -85 | -120
[8 empty] | 2 | -85 | -120
[8 empty] | 2 | -81 | -119
[8 empty] | 2 | -92 | -112
[8 empty] | 2 | -80 | -119
[8 empty] | 2 | -100 | -120
[8 empty] | 2 | -93 | -112
[8 empty] | 2 | -78 | -113
[8 empty] | 2 | -81 | -119
[8 empty] | 2 | -84 | -109
[8 empty] | 2 | -83 | -106
[8 empty] | 2 | -84 | -117
[8 empty] | 2 | -79 | -109
[8 empty] | 2 | -94 | -105
[8 empty] | 2 | -77 | -120
[8 empty] | 2 | -87 | -109
[8 empty] | 2 | -89 | -117
[8 empty] | 2 | -79 | -116
[8 empty] | 2 | -83 | -111
[8 empty] | 2 | -94 | -110
[8 empty] | 2 | -78 | -109
[8 empty] | 2 | -84 | -107
[8 empty] | 2 | -92 | -112
[8 empty] | 2 | -83 | -112
[8 empty] | 2 | -102 | -112
[8 empty] | 2 | -91 | -113
[8 empty] | 2 | -95 | -115
[8 empty] | 2 | -84 | -118
[8 empty] | 2 | -86 | -117
[8 empty] | 2 | -88 | -107
[8 empty] | 2 | -89 | -113
[8 empty] | 2 | -83 | -107
[8 empty] | 2 | -81 | -109
[8 empty] | 2 | -81 | -111
[8 empty] | 2 | -89 | -120
[8 empty] | 2 | -84 | -107
[8 empty] | 2 | -78 | -115
[8 empty] | 2 | -85 | -102
[8 empty] | 2 | -85 | -116
[8 empty] | 2 | -89 | -113
[8 empty] | 2 | -85 | -114
[8 empty] | 2 | -81 | -107
[8 empty] | 2 | -90 | -105
[8 empty] | 2 | -82 | -119
[8 empty] | 2 | -91 | -108
[8 empty] | 2 | -83 | -113
[8 empty] | 2 | -87 | -108
[8 empty] | 2 | -92 | -105
[8 empty] | 2 | -90 | -108
[8 empty] | 2 | -103 | -113
[8 empty] | 2 | -77 | -109
[8 empty] | 2 | -79 | -111
[8 empty] | 2 | -89 | -105
[8 empty] | 2 | -80 | -112
[8 empty] | 2 | -88 | -115
[8 empty] | 2 | -90 | -117
[8 empty] | 2 | -97 | -116
[8 empty] | 2 | -86 | -115
[8 empty] | 2 | -82 | -120
[8 empty] | 2 | -79 | -119
[8 empty] | 2 | -80 | -104
[8 empty] | 2 | -95 | -107
[8 empty] | 2 | -86 | -106
[8 empty] | 2 | -96 | -109
[8 empty] | 2 | -80 | -103
[8 empty] | 2 | -81 | -107
[8 empty] | 2 | -99 | -118
[8 empty] | 2 | -83 | -104
[8 empty] | 2 | -84 | -120
[8 empty] | 2 | -90 | -111
[8 empty] | 2 | -89 | -108
[8 empty] | 2 | -86 | -106
[8 empty] | 2 | -88 | -102
[8 empty] | 2 | -87 | -117
[8 empty] | 2 | -90 | -107
[8 empty] | 2 | -81 | -115
[8 empty] | 2 | -82 | -108
[8 empty] | 2 | -98 | -109
[8 empty] | 2 | -81 | -119
[8 empty] | 2 | -81 | -107
[8 empty] | 2 | -96 | -108
[8 empty] | 2 | -84 | -106
[8 empty] | 2 | -94 | -105
[8 empty] | 2 | -88 | -107
[8 empty] | 2 | -82 | -114
[8 empty] | 2 | -85 | -109
[8 empty] | 2 | -79 | -110
[8 empty] | 2 | -86 | -108
[8 empty] | 2 | -90 | -111
[8 empty] | 2 | -77 | -117
[8 empty] | 2 | -89 | -109
[8 empty] | 2 | -81 | -109
[8 empty] | 2 | -87 | -102
[8 empty] | 2 | -92 | -111
[8 empty] | 2 | -82 | -115
[8 empty] | 2 | -84 | -117
[8 empty] | 2 | -87 | -109
[8 empty] | 2 | -94 | -118
[8 empty] | 2 | -89 | -118
[8 empty] | 2 | -85 | -116
[8 empty] | 2 | -89 | -109
[8 empty] | 2 | -86 | -119
[8 empty] | 2 | -87 | -120
[8 empty] | 2 | -88 | -112
[8 empty] | 2 | -86 | -115
[8 empty] | 2 | -87 | -105
[8 empty] | 2 | -90 | -119
[8 empty] | 2 | -88 | -110
[8 empty] | 2 | -86 | -119
[8 empty] | 2 | -93 | -115
[8 empty] | 2 | -93 | -120
[8 empty] | 2 | -89 | -107
[8 empty] | 2 | -85 | -112
[8 empty] | 2 | -101 | -109
[8 empty] | 2 | -85 | -111
[8 empty] | 2 | -96 | -111
[8 empty] | 2 | -92 | -108
[8 empty] | 2 | -100 | -110
[8 empty] | 2 | -91 | -115
[8 empty] | 2 | -96 | -117
[8 empty] | 2 | -94 | -111
[8 empty] | 2 | -86 | -111
[8 empty] | 2 | -105 | -111
[8 empty] | 2 | -94 | -115
[8 empty] | 2 | -96 | -116
[8 empty] | 2 | -100 | -114
[8 empty] | 2 | -93 | -113
[8 empty] | 2 | -94 | -120
[8 empty] | 2 | -91 | -116
[8 empty] | 2 | -93 | -120
[8 empty] | 2 | -111 | -114
[8 empty] | 2 | -102 | -114
[8 empty] | 2 | -72 | -99
[8 empty] | 2 | -72 | -99
[8 empty] | 2 | -71 | -118
[8 empty] | 3 | -77 | -99
[8 empty] | 3 | -73 | -106
[8 empty] | 3 | -70 | -98
[8 empty] | 3 | -73 | -97
[8 empty] | 3 | -73 | -104
[8 empty] | 3 | -72 | -97
[8 empty] | 3 | -87 | -99
[8 empty] | 3 | -79 | -101
[8 empty] | 3 | -72 | -120
[8 empty] | 3 | -75 | -106
[8 empty] | 3 | -99 | -101
[8 empty] | 3 | -73 | -96
[8 empty] | 3 | -72 | -102
[8 empty] | 3 | -82 | -108
[8 empty] | 3 | -81 | -107
[8 empty] | 3 | -82 | -98
[8 empty] | 3 | -83 | -98
[8 empty] | 3 | -82 | -98
[8 empty] | 3 | -96 | -118
[8 empty] | 4 | -97 | -120
[8 empty] | 4 | -96 | -119
[8 empty] | 4 | -107 | -113
[8 empty] | 4 | -91 | -119
[8 empty] | 4 | -86 | -116
[8 empty] | 4 | -94 | -119
[8 empty] | 4 | -90 | -118
[8 empty] | 4 | -108 | -118
[8 empty] | 4 | -98 | -115
[8 empty] | 4 | -91 | -115
[8 empty] | 4 | -87 | -117
[8 empty] | 4 | -93 | -113
[8 empty] | 4 | -87 | -113
[8 empty] | 4 | -87 | -115
[8 empty] | 4 | -104 | -112
[8 empty] | 4 | -86 | -110
[8 empty] | 4 | -103 | -108
[8 empty] | 4 | -96 | -109
[8 empty] | 4 | -94 | -115
[8 empty] | 4 | -89 | -113
[8 empty] | 4 | -87 | -110
[8 empty] | 4 | -87 | -114
[8 empty] | 4 | -92 | -115
[8 empty] | 4 | -90 | -110
[8 empty] | 4 | -86 | -120
[8 empty] | 4 | -91 | -108
[8 empty] | 4 | -97 | -111
[8 empty] | 4 | -104 | -108
[8 empty] | 4 | -89 | -109
[8 empty] | 4 | -92 | -111
[8 empty] | 4 | -86 | -115
[8 empty] | 4 | -88 | -116
[8 empty] | 4 | -90 | -118
[8 empty] | 4 | -90 | -113
[8 empty] | 4 | -99 | -110
[8 empty] | 4 | -82 | -110
[8 empty] | 4 | -95 | -117
[8 empty] | 4 | -87 | -120
[8 empty] | 4 | -89 | -118
[8 empty] | 4 | -99 | -114
[8 empty] | 4 | -83 | -113
[8 empty] | 4 | -95 | -114
[8 empty] | 4 | -88 | -107
[8 empty] | 4 | -82 | -106
[8 empty] | 4 | -80 | -100
[8 empty] | 4 | -79 | -97
[8 empty] | 4 | -76 | -98
[8 empty] | 4 | -73 | -98
[8 empty] | 4 | -74 | -100
[8 empty] | 4 | -73 | -101
[8 empty] | 4 | -73 | -98
[8 empty] | 4 | -73 | -95
[8 empty] | 5 | -71 | -102
[8 empty] | 5 | -70 | -99
[8 empty] | 5 | -69 | -96
[8 empty] | 5 | -74 | -102
[8 empty] | 5 | -72 | -104
[8 empty] | 5 | -72 | -112
[8 empty] | 5 | -68 | -104
[8 empty] | 5 | -68 | -103
[8 empty] | 5 | -67 | -96
[8 empty] | 5 | -69 | -100
[8 empty] | 5 | -70 | -95
[8 empty] | 5 | -71 | -93
[8 empty] | 5 | -71 | -96
[8 empty] | 5 | -72 | -89
[8 empty] | 5 | -78 | -88
[8 empty] | 5 | -70 | -92
[8 empty] | 5 | -71 | -86
[8 empty] | 5 | -73 | -93
[8 empty] | 5 | -75 | -89
[8 empty] | 5 | -66 | -98
[8 empty] | 5 | -62 | -90
[8 empty] | 5 | -61 | -101
[8 empty] | 5 | -65 | -98
[8 empty] | 5 | -71 | -88
[8 empty] | 5 | -62 | -89
[8 empty] | 5 | -65 | -102
[8 empty] | 5 | -72 | -98
[8 empty] | 5 | -68 | -89
[8 empty] | 5 | -66 | -100
[8 empty] | 5 | -73 | -91
[8 empty] | 5 | -87 | -89
[8 empty] | 5 | -75 | -91
[8 empty] | 5 | -76 | -96
[8 empty] | 5 | -80 | -113
[8 empty] | 5 | -73 | -96
[8 empty] | 5 | -68 | -93
[8 empty] | 5 | -80 | -96
[8 empty] | 5 | -94 | -97
[8 empty] | 5 | -74 | -94
[8 empty] | 5 | -76 | -98
[8 empty] | 5 | -71 | -105
[8 empty] | 5 | -72 | -106
[8 empty] | 5 | -77 | -100
[8 empty] | 5 | -65 | -102
[8 empty] | 5 | -75 | -95
[8 empty] | 5 | -80 | -98
[8 empty] | 5 | -78 | -101
[8 empty] | 5 | -79 | -107
[8 empty] | 5 | -72 | -111
[8 empty] | 5 | -73 | -93
[8 empty] | 5 | -74 | -97
[8 empty] | 5 | -77 | -97
[8 empty] | 5 | -80 | -99
[8 empty] | 5 | -71 | -103
[8 empty] | 5 | -70 | -105
[8 empty] | 5 | -73 | -95
[8 empty] | 5 | -74 | -100
[8 empty] | 5 | -82 | -109
[8 empty] | 5 | -79 | -95
[8 empty] | 5 | -80 | -95
[8 empty] | 5 | -72 | -105
[8 empty] | 5 | -77 | -97
[8 empty] | 5 | -75 | -107
[8 empty] | 5 | -83 | -103
[8 empty] | 5 | -73 | -95
[8 empty] | 5 | -75 | -107
[8 empty] | 5 | -69 | -97
[8 empty] | 5 | -67 | -96
[8 empty] | 5 | -66 | -101
[8 empty] | 5 | -74 | -99
[8 empty] | 5 | -78 | -87
[8 empty] | 5 | -70 | -85
[8 empty] | 5 | -69 | -86
[8 empty] | 5 | -69 | -88
[8 empty] | 5 | -64 | -87
[8 empty] | 5 | -64 | -93
[8 empty] | 5 | -70 | -85
[8 empty] | 5 | -69 | -88
[8 empty] | 5 | -73 | -105
[8 empty] | 5 | -64 | -94
[8 empty] | 5 | -71 | -85
[8 empty] | 5 | -72 | -89
[8 empty] | 5 | -67 | -96
[8 empty] | 5 | -68 | -101
[8 empty] | 5 | -73 | -84
[8 empty] | 5 | -69 | -93
[8 empty] | 5 | -74 | -91
[8 empty] | 5 | -69 | -89
[8 empty] | 5 | -71 | -96
[8 empty] | 5 | -69 | -96
[8 empty] | 5 | -79 | -95
[8 empty] | 5 | -80 | -98
[8 empty] | 5 | -76 | -98
[8 empty] | 5 | -71 | -90
[8 empty] | 5 | -68 | -95
[8 empty] | 5 | -65 | -96
[8 empty] | 5 | -73 | -103
[8 empty] | 5 | -76 | -95
[8 empty] | 5 | -68 | -110
[8 empty] | 5 | -80 | -106
[8 empty] | 5 | -76 | -92
[8 empty] | 5 | -72 | -94
[8 empty] | 5 | -71 | -99
[8 empty] | 5 | -86 | -101
[8 empty] | 5 | -85 | -97
[8 empty] | 5 | -83 | -112
[8 empty] | 5 | -77 | -99
[8 empty] | 5 | -84 | -94
[8 empty] | 5 | -76 | -93
[8 empty] | 5 | -71 | -98
[8 empty] | 5 | -74 | -98
[8 empty] | 5 | -102 | -94
[8 empty] | 5 | -74 | -112
[8 empty] | 5 | -73 | -105
[8 empty] | 5 | -67 | -95
[8 empty] | 5 | -65 | -94
[8 empty] | 5 | -79 | -101
[8 empty] | 5 | -73 | -100
[8 empty] | 5 | -68 | -102
[8 empty] | 5 | -64 | -96
[8 empty] | 5 | -78 | -112
[8 empty] | 5 | -77 | -110
[8 empty] | 5 | -81 | -106
[8 empty] | 5 | -81 | -103
[8 empty] | 5 | -87 | -103
[8 empty] | 6 | -88 | -102
[8 empty] | 6 | -80 | -112
[8 empty] | 6 | -90 | -112
[8 empty] | 6 | -93 | -120
[8 empty] | 6 | -81 | -110
[8 empty] | 6 | -95 | -119
[8 empty] | 6 | -94 | -108
[8 empty] | 6 | -97 | -110
[8 empty] | 6 | -84 | -109
[8 empty] | 6 | -76 | -104
[8 empty] | 6 | -77 | -102
[8 empty] | 6 | -83 | -111
[8 empty] | 6 | -81 | -114
[8 empty] | 6 | -93 | -114
[8 empty] | 6 | -85 | -109
[8 empty] | 6 | -85 | -107
[8 empty] | 6 | -101 | -108
[8 empty] | 6 | -83 | -105
[8 empty] | 6 | -78 | -108
[8 empty] | 6 | -75 | -102
[8 empty] | 6 | -81 | -116
[8 empty] | 6 | -84 | -110
[8 empty] | 6 | -81 | -118
[8 empty] | 6 | -81 | -116
[8 empty] | 6 | -79 | -104
[8 empty] | 6 | -90 | -115
[8 empty] | 6 | -83 | -109
[8 empty] | 6 | -77 | -117
[8 empty] | 6 | -77 | -102
[8 empty] | 6 | -80 | -108
[8 empty] | 6 | -94 | -106
[8 empty] | 6 | -77 | -116
[8 empty] | 6 | -84 | -110
[8 empty] | 6 | -76 | -107
[8 empty] | 6 | -86 | -109
[8 empty] | 6 | -79 | -118
[8 empty] | 6 | -88 | -116
[8 empty] | 6 | -82 | -107
[8 empty] | 6 | -82 | -113
[8 empty] | 6 | -92 | -112
[8 empty] | 6 | -75 | -113
[8 empty] | 6 | -93 | -104
[8 empty] | 6 | -74 | -106
[8 empty] | 6 | -79 | -104
[8 empty] | 6 | -87 | -111
[8 empty] | 6 | -75 | -101
[8 empty] | 6 | -72 | -107
[8 empty] | 6 | -82 | -115
[8 empty] | 6 | -81 | -113
[8 empty] | 6 | -76 | -111
[8 empty] | 6 | -71 | -105
[8 empty] | 6 | -79 | -105
[8 empty] | 6 | -75 | -105
[8 empty] | 6 | -74 | -107
[8 empty] | 6 | -79 | -114
[8 empty] | 6 | -76 | -120
[8 empty] | 6 | -79 | -104
[8 empty] | 6 | -71 | -109
[8 empty] | 6 | -69 | -106
[8 empty] | 6 | -71 | -110
[8 empty] | 6 | -68 | -120
[8 empty] | 6 | -75 | -110
[8 empty] | 6 | -68 | -106
[8 empty] | 6 | -84 | -118
[8 empty] | 6 | -78 | -107
[8 empty] | 6 | -72 | -112
[8 empty] | 6 | -67 | -117
[8 empty] | 6 | -68 | -114
[8 empty] | 6 | -80 | -114
[8 empty] | 6 | -69 | -108
[8 empty] | 6 | -88 | -109
[8 empty] | 6 | -73 | -118
[8 empty] | 6 | -65 | -120
[8 empty] | 6 | -66 | -110
[8 empty] | 6 | -65 | -120
[8 empty] | 6 | -69 | -115
[8 empty] | 6 | -74 | -117
[8 empty] | 6 | -80 | -113
[8 empty] | 6 | -70 | -112
[8 empty] | 6 | -88 | -120
[8 empty] | 6 | -79 | -111
[8 empty] | 6 | -69 | -118
[8 empty] | 6 | -68 | -117
[8 empty] | 6 | -67 | -111
[8 empty] | 6 | -66 | -109
[8 empty] | 6 | -75 | -117
[8 empty] | 6 | -92 | -108
[8 empty] | 6 | -73 | -108
[8 empty] | 6 | -75 | -120
[8 empty] | 6 | -68 | -112
[8 empty] | 6 | -72 | -116
[8 empty] | 6 | -74 | -113
[8 empty] | 6 | -72 | -107
[8 empty] | 6 | -70 | -108
[8 empty] | 6 | -82 | -111
[8 empty] | 6 | -66 | -116
[8 empty] | 6 | -77 | -110
[8 empty] | 6 | -70 | -115
[8 empty] | 6 | -75 | -106
[8 empty] | 6 | -66 | -108
[8 empty] | 6 | -64 | -112
[8 empty] | 6 | -71 | -112
[8 empty] | 6 | -63 | -108
[8 empty] | 6 | -75 | -112
[8 empty] | 6 | -67 | -109
[8 empty] | 6 | -68 | -112
[8 empty] | 6 | -71 | -102
[8 empty] | 6 | -66 | -107
[8 empty] | 6 | -67 | -105
[8 empty] | 6 | -69 | -108
[8 empty] | 6 | -62 | -111
[8 empty] | 6 | -58 | -100
[8 empty] | 6 | -56 | -103
[8 empty] | 6 | -57 | -111
[8 empty] | 6 | -52 | -102
[8 empty] | 6 | -65 | -107
[8 empty] | 6 | -69 | -100
[8 empty] | 6 | -54 | -110
[8 empty] | 6 | -75 | -99
[8 empty] | 6 | -58 | -116
[8 empty] | 6 | -62 | -113
[8 empty] | 6 | -62 | -102
[8 empty] | 6 | -63 | -103
[8 empty] | 6 | -71 | -120
[8 empty] | 6 | -54 | -105
[8 empty] | 6 | -60 | -103
[8 empty] | 6 | -65 | -109
[8 empty] | 6 | -59 | -109
[8 empty] | 6 | -60 | -109
[8 empty] | 6 | -65 | -106
[8 empty] | 6 | -62 | -109
[8 empty] | 6 | -78 | -109
[8 empty] | 6 | -66 | -108
[8 empty] | 6 | -67 | -102
[8 empty] | 6 | -76 | -103
[8 empty] | 6 | -61 | -101
[8 empty] | 6 | -64 | -112
[8 empty] | 6 | -63 | -113
[8 empty] | 6 | -65 | -110
[8 empty] | 6 | -85 | -103
[8 empty] | 6 | -65 | -103
[8 empty] | 6 | -66 | -114
[8 empty] | 6 | -59 | -105
[8 empty] | 6 | -60 | -102
[8 empty] | 6 | -74 | -113
[8 empty] | 6 | -68 | -110
[8 empty] | 6 | -63 | -104
[8 empty] | 6 | -70 | -114
[8 empty] | 6 | -58 | -112
[8 empty] | 6 | -57 | -115
[8 empty] | 6 | -64 | -108
[8 empty] | 6 | -58 | -104
[8 empty] | 6 | -78 | -105
[8 empty] | 6 | -69 | -110
[8 empty] | 6 | -62 | -111
[8 empty] | 6 | -64 | -107
[8 empty] | 6 | -63 | -110
[8 empty] | 6 | -79 | -112
[8 empty] | 6 | -58 | -109
[8 empty] | 6 | -71 | -108
[8 empty] | 6 | -62 | -113
[8 empty] | 6 | -68 | -114
[8 empty] | 6 | -70 | -113
[8 empty] | 6 | -65 | -106
[8 empty] | 6 | -72 | -103
[8 empty] | 6 | -72 | -100
[8 empty] | 6 | -69 | -109
[8 empty] | 6 | -82 | -114
[8 empty] | 6 | -71 | -108
[8 empty] | 6 | -68 | -112
[8 empty] | 6 | -75 | -110
[8 empty] | 6 | -71 | -114
[8 empty] | 6 | -76 | -111
[8 empty] | 6 | -67 | -117
[8 empty] | 6 | -68 | -107
[8 empty] | 6 | -73 | -112
[8 empty] | 6 | -78 | -116
[8 empty] | 6 | -79 | -114
[8 empty] | 6 | -76 | -120
[8 empty] | 6 | -79 | -115
[8 empty] | 6 | -74 | -114
[8 empty] | 6 | -72 | -113
[8 empty] | 6 | -77 | -108
[8 empty] | 6 | -69 | -112
[8 empty] | 6 | -68 | -112
[8 empty] | 6 | -74 | -107
[8 empty] | 6 | -79 | -107
[8 empty] | 6 | -74 | -107
[8 empty] | 6 | -69 | -102
[8 empty] | 6 | -71 | -108
[8 empty] | 7 | -70 | -102
[8 empty] | 7 | -75 | -95
[8 empty] | 7 | -70 | -91
[8 empty] | 7 | -68 | -92
[8 empty] | 7 | -72 | -96
[8 empty] | 7 | -70 | -98
[8 empty] | 7 | -76 | -94
[8 empty] | 7 | -69 | -95
[8 empty] | 7 | -79 | -120
[8 empty] | 7 | -68 | -100
[8 empty] | 7 | -85 | -118
[8 empty] | 7 | -74 | -101
[8 empty] | 7 | -78 | -105
[8 empty] | 7 | -73 | -96
[8 empty] | 7 | -74 | -103
[8 empty] | 7 | -74 | -98
[8 empty] | 7 | -77 | -118
[8 empty] | 7 | -77 | -96
[8 empty] | 7 | -72 | -98
[8 empty] | 7 | -86 | -97
[8 empty] | 7 | -71 | -99
[8 empty] | 7 | -68 | -99
[8 empty] | 7 | -79 | -95
[8 empty] | 7 | -72 | -96
[8 empty] | 7 | -71 | -99
[8 empty] | 7 | -71 | -104
[8 empty] | 7 | -75 | -107
[8 empty] | 7 | -71 | -105
[8 empty] | 7 | -68 | -99
[8 empty] | 7 | -63 | -116
[8 empty] | 7 | -73 | -106
[8 empty] | 7 | -67 | -105
[8 empty] | 7 | -77 | -101
[8 empty] | 7 | -66 | -95
[8 empty] | 7 | -81 | -104
[8 empty] | 7 | -72 | -93
[8 empty] | 7 | -67 | -108
[8 empty] | 7 | -64 | -97
[8 empty] | 7 | -71 | -111
[8 empty] | 7 | -67 | -99
[8 empty] | 7 | -65 | -97
[8 empty] | 7 | -67 | -101
[8 empty] | 7 | -66 | -107
[8 empty] | 7 | -73 | -110
[8 empty] | 7 | -69 | -96
[8 empty] | 7 | -65 | -114
[8 empty] | 7 | -68 | -92
[8 empty] | 7 | -63 | -96
[8 empty] | 7 | -69 | -92
[8 empty] | 7 | -72 | -88
[8 empty] | 7 | -64 | -100
[8 empty] | 7 | -73 | -94
[8 empty] | 7 | -64 | -101
[8 empty] | 7 | -64 | -96
[8 empty] | 7 | -75 | -97
[8 empty] | 7 | -70 | -100
[8 empty] | 7 | -65 | -94
[8 empty] | 7 | -64 | -99
[8 empty] | 7 | -66 | -96
[8 empty] | 7 | -66 | -108
[8 empty] | 7 | -68 | -103
[8 empty] | 7 | -69 | -108
[8 empty] | 7 | -70 | -93
[8 empty] | 7 | -69 | -98
[8 empty] | 7 | -65 | -98
[8 empty] | 7 | -73 | -120
[8 empty] | 7 | -72 | -98
[8 empty] | 7 | -69 | -98
[8 empty] | 7 | -68 | -106
[8 empty] | 7 | -83 | -96
[8 empty] | 7 | -75 | -100
[8 empty] | 7 | -82 | -109
[8 empty] | 7 | -74 | -102
[8 empty] | 7 | -74 | -98
[8 empty] | 7 | -76 | -106
[8 empty] | 7 | -78 | -104
[8 empty] | 7 | -69 | -101
[8 empty] | 7 | -76 | -100
[8 empty] | 7 | -92 | -112
[8 empty] | 7 | -76 | -109
[8 empty] | 7 | -80 | -108
[8 empty] | 7 | -74 | -115
[8 empty] | 7 | -77 | -108
[8 empty] | 7 | -87 | -113
[8 empty] | 7 | -87 | -108
[8 empty] | 7 | -82 | -111
[8 empty] | 7 | -76 | -111
[8 empty] | 7 | -91 | -99
[8 empty] | 7 | -82 | -103
[8 empty] | 7 | -81 | -101
[8 empty] | 7 | -79 | -109
[8 empty] | 7 | -76 | -99
[8 empty] | 7 | -87 | -119
[8 empty] | 7 | -78 | -118
[8 empty] | 7 | -78 | -111
[8 empty] | 7 | -91 | -108
[8 empty] | 7 | -83 | -106
[8 empty] | 7 | -91 | -110
[8 empty] | 7 | -84 | -103
[8 empty] | 7 | -86 | -107
[8 empty] | 7 | -76 | -108
[8 empty] | 7 | -79 | -115
[8 empty] | 7 | -75 | -102
[8 empty] | 7 | -77 | -102
[8 empty] | 7 | -77 | -106
[8 empty] | 7 | -78 | -105
[8 empty] | 7 | -81 | -99
[8 empty] | 7 | -77 | -99
[8 empty] | 7 | -78 | -113
[8 empty] | 7 | -80 | -110
[8 empty] | 7 | -78 | -112
[8 empty] | 7 | -97 | -105
[8 empty] | 7 | -84 | -103
[8 empty] | 7 | -81 | -108
[8 empty] | 7 | -80 | -113
[8 empty] | 7 | -82 | -111
[8 empty] | 7 | -80 | -114
[8 empty] | 7 | -84 | -116
[8 empty] | 7 | -82 | -119
[8 empty] | 7 | -86 | -104
[8 empty] | 7 | -84 | -108
[8 empty] | 7 | -81 | -113
[8 empty] | 7 | -87 | -105
[8 empty] | 7 | -87 | -102
[8 empty] | 7 | -106 | -106
[8 empty] | 7 | -84 | -110
[8 empty] | 7 | -84 | -115
[8 empty] | 7 | -80 | -116
[8 empty] | 7 | -94 | -109
[8 empty] | 7 | -85 | -109
[8 empty] | 7 | -78 | -107
[8 empty] | 7 | -86 | -118
[8 empty] | 7 | -79 | -107
[8 empty] | 7 | -79 | -110
[8 empty] | 7 | -75 | -103
[8 empty] | 7 | -81 | -104
[8 empty] | 7 | -84 | -100
[8 empty] | 7 | -75 | -107
[8 empty] | 7 | -83 | -111
[8 empty] | 7 | -79 | -103
[8 empty] | 7 | -88 | -108
[8 empty] | 7 | -89 | -106
[8 empty] | 7 | -83 | -107
[8 empty] | 7 | -77 | -108
[8 empty] | 7 | -79 | -108
[8 empty] | 7 | -84 | -111
[8 empty] | 7 | -89 | -110
[8 empty] | 7 | -79 | -109
[8 empty] | 7 | -84 | -106
[8 empty] | 7 | -78 | -115
[8 empty] | 7 | -81 | -115
[8 empty] | 7 | -83 | -106
[8 empty] | 7 | -89 | -116
[8 empty] | 7 | -107 | -113
[8 empty] | 7 | -85 | -109
[8 empty] | 7 | -87 | -115
[8 empty] | 7 | -98 | -107
[8 empty] | 7 | -86 | -101
[8 empty] | 7 | -81 | -106
[8 empty] | 7 | -85 | -103
[8 empty] | 7 | -89 | -107
[8 empty] | 7 | -87 | -113
[8 empty] | 7 | -82 | -106
[8 empty] | 7 | -84 | -109
[8 empty] | 7 | -91 | -106
[8 empty] | 7 | -79 | -111
[8 empty] | 7 | -90 | -110
[8 empty] | 7 | -84 | -119
[8 empty] | 7 | -87 | -105
[8 empty] | 7 | -79 | -114
[8 empty] | 7 | -83 | -106
[8 empty] | 7 | -78 | -112
[8 empty] | 7 | -81 | -101
[8 empty] | 7 | -90 | -108
[8 empty] | 7 | -83 | -111
[8 empty] | 7 | -86 | -109
[8 empty] | 7 | -85 | -100
[8 empty] | 7 | -83 | -103
[8 empty] | 7 | -78 | -104
[8 empty] | 7 | -84 | -99
[8 empty] | 7 | -92 | -108
[8 empty] | 7 | -96 | -97
[8 empty] | 7 | -76 | -97
[8 empty] | 7 | -81 | -106
[8 empty] | 7 | -76 | -107
[8 empty] | 7 | -82 | -99
[8 empty] | 7 | -83 | -102
[8 empty] | 7 | -79 | -106
[8 empty] | 7 | -81 | -102
[8 empty] | 7 | -77 | -103
[8 empty] | 7 | -84 | -103
[8 empty] | 7 | -94 | -105
[8 empty] | 7 | -86 | -111
[8 empty] | 7 | -85 | -107
[8 empty] | 7 | -76 | -108
[8 empty] | 7 | -76 | -113
[8 empty] | 7 | -80 | -107
[8 empty] | 7 | -87 | -103
[8 empty] | 7 | -76 | -108
[8 empty] | 7 | -79 | -106
[8 empty] | 7 | -75 | -106
[8 empty] | 7 | -77 | -108
[8 empty] | 7 | -73 | -101
[8 empty] | 7 | -75 | -100
[8 empty] | 7 | -74 | -100
[8 empty] | 7 | -80 | -104
[8 empty] | 7 | -83 | -101
[8 empty] | 7 | -79 | -96
[8 empty] | 7 | -89 | -99
[8 empty] | 7 | -77 | -106
[8 empty] | 7 | -77 | -104
[8 empty] | 7 | -77 | -107
[8 empty] | 8 | -79 | -105
[8 empty] | 8 | -80 | -106
[8 empty] | 8 | -79 | -109
[8 empty] | 8 | -77 | -108
[8 empty] | 8 | -78 | -109
[8 empty] | 8 | -71 | -110
[8 empty] | 8 | -71 | -111
[8 empty] | 8 | -77 | -115
[8 empty] | 8 | -72 | -106
[8 empty] | 8 | -86 | -106
[8 empty] | 8 | -84 | -105
[8 empty] | 8 | -76 | -114
[8 empty] | 8 | -70 | -107
[8 empty] | 8 | -72 | -105
[8 empty] | 8 | -73 | -108
[8 empty] | 8 | -75 | -108
[8 empty] | 8 | -70 | -103
[8 empty] | 8 | -70 | -99
[8 empty] | 8 | -81 | -99
[8 empty] | 8 | -70 | -97
[8 empty] | 8 | -71 | -99
[8 empty] | 8 | -61 | -100
[8 empty] | 8 | -64 | -95
[8 empty] | 8 | -66 | -97
[8 empty] | 8 | -62 | -103
[8 empty] | 8 | -61 | -101
[8 empty] | 8 | -56 | -94
[8 empty] | 8 | -62 | -94
[8 empty] | 8 | -65 | -98
[8 empty] | 8 | -64 | -98
[8 empty] | 8 | -66 | -94
[8 empty] | 8 | -65 | -94
[8 empty] | 8 | -68 | -100
[8 empty] | 8 | -63 | -91
[8 empty] | 8 | -60 | -93
[8 empty] | 8 | -71 | -94
[8 empty] | 8 | -73 | -94
[8 empty] | 8 | -66 | -95
[8 empty] | 8 | -71 | -106
[8 empty] | 8 | -57 | -99
[8 empty] | 8 | -61 | -101
[8 empty] | 8 | -60 | -93
[8 empty] | 8 | -51 | -99
[8 empty] | 8 | -57 | -98
[8 empty] | 8 | -51 | -88
[8 empty] | 8 | -51 | -93
[8 empty] | 8 | -58 | -88
[8 empty] | 8 | -57 | -95
[8 empty] | 8 | -51 | -95
[8 empty] | 8 | -54 | -90
[8 empty] | 8 | -62 | -89
[8 empty] | 8 | -50 | -88
[8 empty] | 8 | -49 | -89
[8 empty] | 8 | -52 | -87
[8 empty] | 8 | -56 | -89
[8 empty] | 8 | -56 | -90
[8 empty] | 8 | -56 | -88
[8 empty] | 8 | -54 | -86
[8 empty] | 8 | -54 | -86
[8 empty] | 8 | -55 | -83
[8 empty] | 8 | -55 | -84
[8 empty] | 8 | -54 | -83
[8 empty] | 8 | -51 | -85
[8 empty] | 8 | -52 | -87
[8 empty] | 8 | -52 | -86
[8 empty] | 8 | -51 | -86
[8 empty] | 8 | -59 | -91
[8 empty] | 8 | -56 | -93
[8 empty] | 8 | -69 | -94
[8 empty] | 9 | -69 | -91
[8 empty] | 9 | -68 | -90
[8 empty] | 9 | -69 | -99
[8 empty] | 9 | -72 | -93
[8 empty] | 9 | -69 | -98
[8 empty] | 9 | -63 | -88
[8 empty] | 9 | -65 | -95
[8 empty] | 9 | -67 | -95
[8 empty] | 9 | -76 | -96
[8 empty] | 9 | -61 | -101
[8 empty] | 9 | -61 | -97
[8 empty] | 9 | -71 | -96
[8 empty] | 9 | -69 | -106
[8 empty] | 9 | -66 | -96
[8 empty] | 9 | -67 | -101
[8 empty] | 9 | -64 | -98
[8 empty] | 9 | -65 | -102
[8 empty] | 9 | -65 | -96
[8 empty] | 9 | -63 | -98
[8 empty] | 9 | -64 | -95
[8 empty] | 9 | -78 | -101
[8 empty] | 9 | -73 | -94
[8 empty] | 9 | -70 | -97
[8 empty] | 9 | -64 | -97
[8 empty] | 9 | -67 | -93
[8 empty] | 9 | -73 | -94
[8 empty] | 9 | -76 | -98
[8 empty] | 9 | -69 | -114
[8 empty] | 9 | -64 | -92
[8 empty] | 9 | -72 | -100
[8 empty] | 9 | -68 | -99
[8 empty] | 9 | -75 | -103
[8 empty] | 9 | -62 | -89
[8 empty] | 9 | -65 | -97
[8 empty] | 9 | -74 | -98
[8 empty] | 9 | -75 | -100
[8 empty] | 9 | -62 | -97
[8 empty] | 9 | -63 | -98
[8 empty] | 9 | -62 | -98
[8 empty] | 9 | -63 | -97
[8 empty] | 9 | -67 | -92
[8 empty] | 9 | -59 | -100
[8 empty] | 9 | -72 | -90
[8 empty] | 9 | -69 | -86
[8 empty] | 9 | -64 | -92
[8 empty] | 9 | -74 | -95
[8 empty] | 9 | -72 | -90
[8 empty] | 9 | -64 | -93
[8 empty] | 9 | -61 | -88
[8 empty] | 9 | -64 | -103
[8 empty] | 9 | -69 | -103
[8 empty] | 9 | -62 | -107
[8 empty] | 9 | -84 | -100
[8 empty] | 9 | -66 | -95
[8 empty] | 9 | -64 | -97
[8 empty] | 9 | -74 | -95
[8 empty] | 9 | -74 | -102
[8 empty] | 9 | -75 | -97
[8 empty] | 9 | -76 | -100
[8 empty] | 9 | -77 | -120
[8 empty] | 9 | -78 | -100
[8 empty] | 9 | -72 | -100
[8 empty] | 9 | -75 | -108
[8 empty] | 9 | -69 | -97
[8 empty] | 9 | -76 | -111
[8 empty] | 9 | -75 | -107
[8 empty] | 9 | -86 | -100
[8 empty] | 9 | -69 | -98
[8 empty] | 9 | -78 | -96
[8 empty] | 9 | -84 | -104
[8 empty] | 9 | -74 | -101
[8 empty] | 9 | -70 | -107
[8 empty] | 9 | -67 | -101
[8 empty] | 9 | -71 | -98
[8 empty] | 9 | -78 | -101
[8 empty] | 9 | -85 | -94
[8 empty] | 9 | -72 | -115
[8 empty] | 9 | -78 | -103
[8 empty] | 9 | -72 | -105
[8 empty] | 9 | -78 | -98
[8 empty] | 9 | -76 | -101
[8 empty] | 9 | -75 | -102
[8 empty] | 9 | -73 | -104
[8 empty] | 9 | -78 | -108
[8 empty] | 9 | -83 | -108
[8 empty] | 9 | -78 | -103
[8 empty] | 9 | -76 | -111
[8 empty] | 9 | -75 | -110
[8 empty] | 9 | -74 | -102
[8 empty] | 9 | -87 | -112
[8 empty] | 9 | -73 | -107
[8 empty] | 9 | -85 | -103
[8 empty] | 9 | -94 | -104
[8 empty] | 9 | -76 | -102
[8 empty] | 9 | -96 | -103
[8 empty] | 9 | -73 | -97
[8 empty] | 9 | -77 | -103
[8 empty] | 9 | -80 | -104
[8 empty] | 9 | -75 | -105
[8 empty] | 9 | -76 | -107
[8 empty] | 9 | -77 | -97
[8 empty] | 9 | -77 | -97
[8 empty] | 9 | -75 | -99
[8 empty] | 9 | -78 | -105
[8 empty] | 9 | -74 | -102
[8 empty] | 9 | -87 | -101
[8 empty] | 9 | -85 | -110
[8 empty] | 9 | -98 | -101
[8 empty] | 9 | -83 | -99
[8 empty] | 9 | -82 | -108
[8 empty] | 9 | -78 | -101
[8 empty] | 9 | -76 | -106
[8 empty] | 9 | -79 | -98
[8 empty] | 9 | -83 | -99
[8 empty] | 9 | -74 | -103
[8 empty] | 9 | -76 | -99
[8 empty] | 9 | -86 | -98
[8 empty] | 9 | -76 | -98
[8 empty] | 9 | -76 | -95
[8 empty] | 9 | -77 | -115
[8 empty] | 9 | -75 | -102
[8 empty] | 9 | -97 | -100
[8 empty] | 9 | -81 | -99
[8 empty] | 9 | -75 | -119
[8 empty] | 9 | -87 | -101
[8 empty] | 9 | -85 | -107
[8 empty] | 9 | -84 | -120
[8 empty] | 9 | -84 | -110
[8 empty] | 9 | -85 | -120
[8 empty] | 9 | -82 | -113
[8 empty] | 9 | -83 | -106
[8 empty] | 9 | -79 | -106
[8 empty] | 9 | -78 | -105
[8 empty] | 9 | -87 | -111
[8 empty] | 9 | -81 | -107
[8 empty] | 9 | -93 | -105
[8 empty] | 9 | -85 | -108
[8 empty] | 9 | -84 | -109
[8 empty] | 9 | -85 | -112
[8 empty] | 9 | -83 | -100
[8 empty] | 9 | -81 | -103
[8 empty] | 9 | -79 | -109
[8 empty] | 9 | -81 | -114
[8 empty] | 9 | -80 | -103
[8 empty] | 9 | -80 | -104
[8 empty] | 9 | -79 | -110
[8 empty] | 9 | -79 | -120
[8 empty] | 9 | -83 | -106
[8 empty] | 9 | -90 | -104
[8 empty] | 9 | -84 | -108
[8 empty] | 9 | -77 | -101
[8 empty] | 9 | -79 | -113
[8 empty] | 9 | -81 | -104
[8 empty] | 9 | -77 | -114
[8 empty] | 9 | -86 | -109
[8 empty] | 9 | -76 | -113
[8 empty] | 9 | -74 | -106
[8 empty] | 9 | -86 | -109
[8 empty] | 9 | -80 | -105
[8 empty] | 9 | -83 | -112
[8 empty] | 9 | -96 | -105
[8 empty] | 9 | -80 | -107
[8 empty] | 9 | -103 | -120
[8 empty] | 9 | -77 | -109
[8 empty] | 9 | -77 | -110
[8 empty] | 9 | -78 | -102
[8 empty] | 9 | -75 | -102
[8 empty] | 9 | -77 | -120
[8 empty] | 9 | -72 | -107
[8 empty] | 9 | -82 | -107
[8 empty] | 9 | -78 | -114
[8 empty] | 9 | -70 | -107
[8 empty] | 9 | -76 | -109
[8 empty] | 9 | -73 | -112
[8 empty] | 9 | -80 | -99
[8 empty] | 9 | -77 | -105
[8 empty] | 9 | -73 | -110
[8 empty] | 9 | -75 | -103
[8 empty] | 9 | -77 | -108
[8 empty] | 9 | -78 | -101
[8 empty] | 9 | -73 | -106
[8 empty] | 9 | -78 | -117
[8 empty] | 9 | -71 | -113
[8 empty] | 9 | -78 | -99
[8 empty] | 9 | -75 | -105
[8 empty] | 9 | -70 | -105
[8 empty] | 9 | -78 | -106
[8 empty] | 9 | -74 | -106
[8 empty] | 9 | -75 | -96
[8 empty] | 9 | -72 | -103
[8 empty] | 9 | -64 | -101
[8 empty] | 9 | -66 | -101
[8 empty] | 9 | -77 | -99
[8 empty] | 9 | -71 | -97
[8 empty] | 9 | -63 | -107
[8 empty] | 9 | -66 | -106
[8 empty] | 9 | -71 | -103
[8 empty] | 9 | -73 | -98
[8 empty] | 9 | -78 | -96
[8 empty] | 9 | -63 | -105
[8 empty] | 9 | -67 | -95
[8 empty] | 9 | -82 | -95
[8 empty] | 9 | -64 | -100
[8 empty] | 9 | -69 | -105
[8 empty] | 9 | -69 | -100
[8 empty] | 9 | -90 | -104
[8 empty] | 9 | -66 | -105
[8 empty] | 9 | -67 | -102
[8 empty] | 9 | -66 | -106
[8 empty] | 9 | -69 | -102
[8 empty] | 9 | -76 | -101
[8 empty] | 9 | -79 | -97
[8 empty] | 9 | -75 | -103
[8 empty] | 9 | -70 | -103
[8 empty] | 9 | -68 | -96
[8 empty] | 9 | -70 | -93
[8 empty] | 9 | -72 | -101
[8 empty] | 9 | -70 | -96
[8 empty] | 9 | -66 | -95
[8 empty] | 9 | -68 | -104
[8 empty] | 9 | -65 | -98
[8 empty] | 9 | -65 | -97
[8 empty] | 9 | -64 | -91
[8 empty] | 9 | -70 | -107
[8 empty] | 9 | -77 | -102
[8 empty] | 9 | -71 | -101
[8 empty] | 9 | -78 | -102
[8 empty] | 9 | -72 | -93
[8 empty] | 9 | -74 | -96
[8 empty] | 9 | -65 | -95
[8 empty] | 9 | -63 | -91
[8 empty] | 9 | -71 | -91
[8 empty] | 9 | -71 | -92
[8 empty] | 9 | -74 | -90
[8 empty] | 9 | -72 | -90
[8 empty] | 9 | -72 | -94
[8 empty] | 9 | -72 | -94
[8 empty] | 9 | -86 | -110
[8 empty] | 9 | -96 | -104
[8 empty] | 10 | -95 | -101
[8 empty] | 10 | -74 | -101
[8 empty] | 10 | -85 | -99
[8 empty] | 10 | -89 | -109
[8 empty] | 10 | -76 | -106
[8 empty] | 10 | -76 | -114
[8 empty] | 10 | -82 | -100
[8 empty] | 10 | -77 | -119
[8 empty] | 10 | -90 | -102
[8 empty] | 10 | -75 | -104
[8 empty] | 10 | -78 | -103
[8 empty] | 10 | -77 | -105
[8 empty] | 10 | -79 | -111
[8 empty] | 10 | -71 | -116
[8 empty] | 10 | -73 | -105
[8 empty] | 10 | -70 | -108
[8 empty] | 10 | -84 | -114
[8 empty] | 10 | -78 | -105
[8 empty] | 10 | -86 | -120
[8 empty] | 10 | -74 | -120
[8 empty] | 10 | -83 | -117
[8 empty] | 10 | -88 | -100
[8 empty] | 10 | -73 | -111
[8 empty] | 10 | -78 | -100
[8 empty] | 10 | -81 | -96
[8 empty] | 10 | -72 | -109
[8 empty] | 10 | -75 | -99
[8 empty] | 10 | -67 | -107
[8 empty] | 10 | -67 | -102
[8 empty] | 10 | -68 | -96
[8 empty] | 10 | -67 | -98
[8 empty] | 10 | -69 | -101
[8 empty] | 10 | -71 | -111
[8 empty] | 10 | -67 | -99
[8 empty] | 10 | -69 | -101
[8 empty] | 10 | -74 | -110
[8 empty] | 10 | -72 | -105
[8 empty] | 10 | -66 | -107
[8 empty] | 10 | -62 | -99
[8 empty] | 10 | -60 | -108
[8 empty] | 10 | -68 | -104
[8 empty] | 10 | -66 | -109
[8 empty] | 10 | -85 | -112
[8 empty] | 10 | -64 | -101
[8 empty] | 10 | -70 | -106
[8 empty] | 10 | -81 | -104
[8 empty] | 10 | -60 | -105
[8 empty] | 10 | -66 | -105
[8 empty] | 10 | -57 | -103
[8 empty] | 10 | -70 | -95
[8 empty] | 10 | -64 | -102
[8 empty] | 10 | -64 | -97
[8 empty] | 10 | -58 | -96
[8 empty] | 10 | -56 | -99
[8 empty] | 10 | -60 | -99
[8 empty] | 10 | -55 | -95
[8 empty] | 10 | -56 | -104
[8 empty] | 10 | -66 | -104
[8 empty] | 10 | -67 | -99
[8 empty] | 10 | -71 | -114
[8 empty] | 10 | -58 | -96
[8 empty] | 10 | -82 | -115
[8 empty] | 10 | -61 | -108
[8 empty] | 10 | -64 | -117
[8 empty] | 10 | -60 | -100
[8 empty] | 10 | -60 | -103
[8 empty] | 10 | -56 | -99
[8 empty] | 10 | -56 | -105
[8 empty] | 10 | -62 | -98
[8 empty] | 10 | -59 | -105
[8 empty] | 10 | -64 | -104
[8 empty] | 10 | -69 | -98
[8 empty] | 10 | -64 | -102
[8 empty] | 10 | -61 | -106
[8 empty] | 10 | -55 | -110
[8 empty] | 10 | -58 | -99
[8 empty] | 10 | -58 | -102
[8 empty] | 10 | -66 | -95
[8 empty] | 10 | -61 | -95
[8 empty] | 10 | -55 | -112
[8 empty] | 10 | -59 | -108
[8 empty] | 10 | -55 | -112
[8 empty] | 10 | -58 | -107
[8 empty] | 10 | -62 | -104
[8 empty] | 10 | -62 | -96
[8 empty] | 10 | -74 | -109
[8 empty] | 10 | -56 | -109
[8 empty] | 10 | -52 | -98
[8 empty] | 10 | -54 | -104
[8 empty] | 10 | -59 | -94
[8 empty] | 10 | -64 | -96
[8 empty] | 10 | -54 | -111
[8 empty] | 10 | -51 | -105
[8 empty] | 10 | -55 | -102
[8 empty] | 10 | -62 | -109
[8 empty] | 10 | -50 | -96
[8 empty] | 10 | -50 | -103
[8 empty] | 10 | -53 | -100
[8 empty] | 10 | -48 | -102
[8 empty] | 10 | -60 | -99
[8 empty] | 10 | -49 | -100
[8 empty] | 10 | -55 | -105
[8 empty] | 10 | -60 | -108
[8 empty] | 10 | -52 | -110
[8 empty] | 10 | -50 | -98
[8 empty] | 10 | -53 | -115
[8 empty] | 10 | -57 | -101
[8 empty] | 10 | -61 | -103
[8 empty] | 10 | -58 | -102
[8 empty] | 10 | -62 | -101
[8 empty] | 10 | -61 | -99
[8 empty] | 10 | -59 | -96
[8 empty] | 10 | -59 | -102
[8 empty] | 10 | -55 | -101
[8 empty] | 10 | -59 | -111
[8 empty] | 10 | -59 | -111
[8 empty] | 10 | -55 | -106
[8 empty] | 10 | -56 | -96
[8 empty] | 10 | -62 | -103
[8 empty] | 10 | -54 | -109
[8 empty] | 10 | -56 | -118
[8 empty] | 10 | -62 | -107
[8 empty] | 10 | -55 | -107
[8 empty] | 10 | -70 | -105
[8 empty] | 10 | -67 | -104
[8 empty] | 10 | -64 | -107
[8 empty] | 10 | -58 | -107
[8 empty] | 10 | -63 | -106
[8 empty] | 10 | -70 | -110
[8 empty] | 10 | -58 | -108
[8 empty] | 10 | -67 | -119
[8 empty] | 10 | -59 | -112
[8 empty] | 10 | -62 | -101
[8 empty] | 10 | -61 | -107
[8 empty] | 10 | -61 | -103
[8 empty] | 10 | -66 | -104
[8 empty] | 10 | -62 | -113
[8 empty] | 10 | -58 | -107
[8 empty] | 10 | -61 | -117
[8 empty] | 10 | -64 | -107
[8 empty] | 10 | -73 | -109
[8 empty] | 10 | -79 | -107
[8 empty] | 10 | -64 | -112
[8 empty] | 10 | -71 | -112
[8 empty] | 10 | -69 | -99
[8 empty] | 10 | -60 | -118
[8 empty] | 10 | -69 | -101
[8 empty] | 10 | -62 | -101
[8 empty] | 10 | -64 | -112
[8 empty] | 10 | -70 | -105
[8 empty] | 10 | -86 | -103
[8 empty] | 10 | -75 | -104
[8 empty] | 10 | -75 | -103
[8 empty] | 10 | -67 | -116
[8 empty] | 10 | -65 | -103
[8 empty] | 10 | -72 | -106
[8 empty] | 10 | -64 | -107
[8 empty] | 10 | -69 | -102
[8 empty] | 10 | -71 | -109
[8 empty] | 10 | -61 | -108
[8 empty] | 10 | -71 | -103
[8 empty] | 10 | -69 | -110
[8 empty] | 10 | -73 | -118
[8 empty] | 10 | -70 | -102
[8 empty] | 10 | -71 | -107
[8 empty] | 10 | -74 | -97
[8 empty] | 10 | -64 | -100
[8 empty] | 10 | -67 | -102
[8 empty] | 10 | -75 | -105
[8 empty] | 10 | -81 | -106
[8 empty] | 10 | -65 | -95
[8 empty] | 10 | -70 | -99
[8 empty] | 10 | -60 | -107
[8 empty] | 10 | -67 | -107
[8 empty] | 10 | -66 | -103
[8 empty] | 10 | -59 | -92
[8 empty] | 10 | -64 | -105
[8 empty] | 10 | -62 | -108
[8 empty] | 10 | -61 | -105
[8 empty] | 10 | -61 | -98
[8 empty] | 10 | -63 | -103
[8 empty] | 10 | -66 | -98
[8 empty] | 10 | -67 | -109
[8 empty] | 10 | -64 | -97
[8 empty] | 10 | -62 | -92
[8 empty] | 10 | -60 | -110
[8 empty] | 10 | -61 | -92
[8 empty] | 10 | -59 | -100
[8 empty] | 10 | -65 | -96
[8 empty] | 10 | -60 | -99
[8 empty] | 10 | -57 | -111
[8 empty] | 10 | -60 | -97
[8 empty] | 10 | -66 | -102
[8 empty] | 10 | -64 | -99
[8 empty] | 10 | -60 | -95
[8 empty] | 10 | -60 | -96
[8 empty] | 10 | -58 | -89
[8 empty] | 10 | -61 | -90
[8 empty] | 10 | -69 | -99
[8 empty] | 10 | -63 | -103
[8 empty] | 10 | -78 | -97
[8 empty] | 10 | -59 | -95
[8 empty] | 10 | -57 | -98
[8 empty] | 10 | -59 | -87
[8 empty] | 10 | -66 | -87
[8 empty] | 10 | -65 | -87
[8 empty] | 10 | -60 | -87
[8 empty] | 10 | -68 | -85
[8 empty] | 10 | -57 | -85
[8 empty] | 10 | -66 | -84
[8 empty] | 10 | -56 | -80
[8 empty] | 10 | -58 | -86
[8 empty] | 10 | -52 | -91
[8 empty] | 10 | -61 | -110
[8 empty] | 10 | -54 | -93
[8 empty] | 10 | -54 | -100
[8 empty] | 10 | -64 | -90
[8 empty] | 10 | -54 | -89
[8 empty] | 10 | -49 | -89
[8 empty] | 10 | -51 | -91
[8 empty] | 10 | -54 | -87
[8 empty] | 10 | -69 | -84
[8 empty] | 10 | -58 | -87
[8 empty] | 10 | -69 | -84
[8 empty] | 10 | -69 | -83
[8 empty] | 10 | -63 | -85
[8 empty] | 10 | -52 | -85
[8 empty] | 11 | -47 | -82
[8 empty] | 11 | -59 | -104
[8 empty] | 11 | -47 | -103
[8 empty] | 11 | -60 | -83
[8 empty] | 11 | -65 | -112
[8 empty] | 11 | -51 | -86
[8 empty] | 11 | -62 | -86
[8 empty] | 11 | -58 | -89
[8 empty] | 11 | -59 | -88
[8 empty] | 11 | -64 | -87
[8 empty] | 11 | -60 | -86
[8 empty] | 11 | -69 | -88
[8 empty] | 11 | -60 | -83
[8 empty] | 11 | -67 | -87
[8 empty] | 11 | -62 | -92
[8 empty] | 11 | -49 | -92
[8 empty] | 11 | -60 | -91
[8 empty] | 11 | -59 | -102
[8 empty] | 11 | -55 | -85
[8 empty] | 11 | -51 | -87
[8 empty] | 11 | -55 | -83
[8 empty] | 11 | -59 | -90
[8 empty] | 11 | -57 | -90
[8 empty] | 11 | -51 | -90
[8 empty] | 11 | -49 | -91
[8 empty] | 11 | -53 | -88
[8 empty] | 11 | -54 | -94
[8 empty] | 11 | -55 | -88
[8 empty] | 11 | -60 | -85
[8 empty] | 11 | -54 | -89
[8 empty] | 11 | -57 | -85
[8 empty] | 11 | -65 | -81
[8 empty] | 11 | -63 | -83
[8 empty] | 11 | -62 | -93
[8 empty] | 11 | -61 | -91
[8 empty] | 11 | -62 | -93
[8 empty] | 11 | -62 | -96
[8 empty] | 11 | -62 | -95
[8 empty] | 11 | -62 | -88
[8 empty] | 11 | -59 | -89
[8 empty] | 11 | -57 | -93
[8 empty] | 11 | -60 | -94
[8 empty] | 11 | -63 | -95
[8 empty] | 11 | -72 | -107
[8 empty] | 11 | -59 | -98
[8 empty] | 11 | -83 | -92
[8 empty] | 11 | -61 | -114
[8 empty] | 11 | -61 | -100
[8 empty] | 11 | -67 | -97
[8 empty] | 11 | -74 | -109
[8 empty] | 11 | -66 | -107
[8 empty] | 11 | -68 | -95
[8 empty] | 11 | -64 | -99
[8 empty] | 11 | -61 | -90
[8 empty] | 11 | -55 | -91
[8 empty] | 11 | -64 | -89
[8 empty] | 11 | -78 | -99
[8 empty] | 11 | -66 | -96
[8 empty] | 11 | -61 | -94
[8 empty] | 11 | -62 | -93
[8 empty] | 11 | -65 | -97
[8 empty] | 11 | -66 | -95
[8 empty] | 11 | -63 | -98
[8 empty] | 11 | -56 | -102
[8 empty] | 11 | -57 | -90
[8 empty] | 11 | -53 | -90
[8 empty] | 11 | -52 | -87
[8 empty] | 11 | -63 | -91
[8 empty] | 11 | -54 | -91
[8 empty] | 11 | -53 | -92
[8 empty] | 11 | -61 | -93
[8 empty] | 11 | -54 | -90
[8 empty] | 11 | -55 | -93
[8 empty] | 11 | -61 | -104
[8 empty] | 11 | -58 | -103
[8 empty] | 11 | -56 | -89
[8 empty] | 11 | -58 | -105
[8 empty] | 11 | -62 | -107
[8 empty] | 11 | -67 | -102
[8 empty] | 11 | -67 | -97
[8 empty] | 11 | -66 | -95
[8 empty] | 11 | -71 | -104
[8 empty] | 11 | -66 | -94
[8 empty] | 11 | -71 | -104
[8 empty] | 11 | -89 | -105
[8 empty] | 11 | -66 | -107
[8 empty] | 11 | -70 | -108
[8 empty] | 11 | -73 | -120
[8 empty] | 11 | -76 | -109
[8 empty] | 11 | -78 | -103
[8 empty] | 11 | -71 | -102
[8 empty] | 11 | -77 | -108
[8 empty] | 11 | -76 | -104
[8 empty] | 11 | -78 | -108
[8 empty] | 11 | -73 | -106
[8 empty] | 11 | -72 | -105
[8 empty] | 11 | -72 | -111
[8 empty] | 11 | -81 | -115
[8 empty] | 11 | -80 | -120
[8 empty] | 11 | -76 | -110
[8 empty] | 11 | -84 | -109
[8 empty] | 11 | -76 | -109
[8 empty] | 11 | -77 | -112
[8 empty] | 11 | -93 | -116
[8 empty] | 11 | -78 | -111
[8 empty] | 11 | -80 | -117
[8 empty] | 11 | -94 | -105
[8 empty] | 11 | -83 | -117
[8 empty] | 11 | -77 | -110
[8 empty] | 11 | -85 | -109

## Raw-Bean Medical.out
Marker | Frequency | RSSI | Frequency | RSSI
1 | 868.7875 | -41 | 866.4375 | -85
1 | 868.7875 | -39 | 866.4375 | -81
1 | 868.7875 | -46 | 866.4375 | -78
1 | 868.7875 | -45 | 866.4375 | -84
1 | 868.7875 | -46 | 866.4375 | -78
1 | 868.7875 | -47 | 866.4375 | -78
1 | 868.7875 | -47 | 866.4375 | -85
1 | 868.7875 | -39 | 866.4375 | -79
1 | 868.7875 | -43 | 866.4375 | -81
1 | 868.7875 | -48 | 866.4375 | -79
1 | 868.7875 | -38 | 866.4375 | -82
1 | 868.7875 | -43 | 866.4375 | -77
1 | 868.7875 | -37 | 866.4375 | -72
1 | 868.7875 | -46 | 866.4375 | -75
1 | 868.7875 | -37 | 866.4375 | -83
1 | 868.7875 | -39 | 866.4375 | -82
1 | 868.7875 | -53 | 866.4375 | -74
1 | 868.7875 | -38 | 866.4375 | -76
1 | 868.7875 | -38 | 866.4375 | -88
1 | 868.7875 | -45 | 866.4375 | -79
1 | 868.7875 | -41 | 866.4375 | -80
1 | 868.7875 | -52 | 866.4375 | -75
1 | 868.7875 | -50 | 866.4375 | -82
1 | 868.7875 | -51 | 866.4375 | -87
1 | 868.7875 | -43 | 866.4375 | -101
1 | 868.7875 | -45 | 866.4375 | -85
1 | 868.7875 | -38 | 866.4375 | -78
1 | 868.7875 | -40 | 866.4375 | -78
1 | 868.7875 | -44 | 866.4375 | -76
1 | 868.7875 | -49 | 866.4375 | -84
1 | 868.7875 | -44 | 866.4375 | -78
1 | 868.7875 | -42 | 866.4375 | -93
1 | 868.7875 | -46 | 866.4375 | -79
1 | 868.7875 | -47 | 866.4375 | -92
1 | 868.7875 | -44 | 866.4375 | -78
1 | 868.7875 | -44 | 866.4375 | -84
1 | 868.7875 | -46 | 866.4375 | -84
1 | 868.7875 | -45 | 866.4375 | -90
1 | 868.7875 | -42 | 866.4375 | -83
1 | 868.7875 | -51 | 866.4375 | -84
1 | 868.7875 | -41 | 866.4375 | -78
1 | 868.7875 | -37 | 866.4375 | -77
1 | 868.7875 | -38 | 866.4375 | -89
1 | 868.7875 | -38 | 866.4375 | -77
1 | 868.7875 | -42 | 866.4375 | -85
1 | 868.7875 | -33 | 866.4375 | -73
1 | 868.7875 | -35 | 866.4375 | -80
1 | 868.7875 | -41 | 866.4375 | -94
1 | 868.7875 | -43 | 866.4375 | -80
1 | 868.7875 | -46 | 866.4375 | -76
1 | 868.7875 | -42 | 866.4375 | -79
1 | 868.7875 | -40 | 866.4375 | -78
1 | 868.7875 | -44 | 866.4375 | -80
1 | 868.7875 | -49 | 866.4375 | -81
1 | 868.7875 | -43 | 866.4375 | -75
1 | 868.7875 | -51 | 866.4375 | -80
1 | 868.7875 | -42 | 866.4375 | -78
1 | 868.7875 | -47 | 866.4375 | -76
1 | 868.7875 | -40 | 866.4375 | -96
1 | 868.7875 | -43 | 866.4375 | -79
1 | 868.7875 | -43 | 866.4375 | -80
1 | 868.7875 | -49 | 866.4375 | -85
1 | 868.7875 | -40 | 866.4375 | -75
1 | 868.7875 | -42 | 866.4375 | -82
1 | 868.7875 | -37 | 866.4375 | -81
1 | 868.7875 | -41 | 866.4375 | -79
1 | 868.7875 | -41 | 866.4375 | -80
1 | 868.7875 | -42 | 866.4375 | -83
1 | 868.7875 | -36 | 866.4375 | -92
1 | 868.7875 | -51 | 866.4375 | -77
1 | 868.7875 | -39 | 866.4375 | -74
1 | 868.7875 | -49 | 866.4375 | -98
1 | 868.7875 | -50 | 866.4375 | -89
1 | 868.7875 | -46 | 866.4375 | -93
1 | 868.7875 | -49 | 866.4375 | -76
1 | 868.7875 | -50 | 866.4375 | -90
1 | 868.7875 | -47 | 866.4375 | -91
1 | 868.7875 | -43 | 866.4375 | -80
1 | 868.7875 | -38 | 866.4375 | -79
1 | 868.7875 | -43 | 866.4375 | -82
1 | 868.7875 | -38 | 866.4375 | -76
1 | 868.7875 | -48 | 866.4375 | -84
1 | 868.7875 | -38 | 866.4375 | -82
1 | 868.7875 | -33 | 866.4375 | -80
1 | 868.7875 | -36 | 866.4375 | -82
1 | 868.7875 | -37 | 866.4375 | -80
1 | 868.7875 | -38 | 866.4375 | -88
1 | 868.7875 | -38 | 866.4375 | -84
1 | 868.7875 | -36 | 866.4375 | -74
1 | 868.7875 | -49 | 866.4375 | -89
1 | 868.7875 | -39 | 866.4375 | -92
1 | 868.7875 | -40 | 866.4375 | -97
1 | 868.7875 | -62 | 866.4375 | -74
1 | 868.7875 | -39 | 866.4375 | -80
1 | 868.7875 | -43 | 866.4375 | -87
1 | 868.7875 | -37 | 866.4375 | -80
1 | 868.7875 | -33 | 866.4375 | -81
1 | 868.7875 | -40 | 866.4375 | -84
1 | 868.7875 | -39 | 866.4375 | -75
1 | 868.7875 | -38 | 866.4375 | -82
1 | 868.7875 | -36 | 866.4375 | -74
1 | 868.7875 | -36 | 866.4375 | -78
1 | 868.7875 | -34 | 866.4375 | -83
1 | 868.7875 | -36 | 866.4375 | -84
1 | 868.7875 | -36 | 866.4375 | -74
1 | 868.7875 | -48 | 866.4375 | -89
1 | 868.7875 | -35 | 866.4375 | -93
1 | 868.7875 | -38 | 866.4375 | -81
1 | 868.7875 | -37 | 866.4375 | -85
1 | 868.7875 | -41 | 866.4375 | -91
1 | 868.7875 | -37 | 866.4375 | -72
1 | 868.7875 | -38 | 866.4375 | -86
1 | 868.7875 | -38 | 866.4375 | -78
1 | 868.7875 | -38 | 866.4375 | -78
1 | 868.7875 | -46 | 866.4375 | -79
1 | 868.7875 | -42 | 866.4375 | -82
1 | 868.7875 | -45 | 866.4375 | -77
1 | 868.7875 | -42 | 866.4375 | -94
1 | 868.7875 | -37 | 866.4375 | -80
1 | 868.7875 | -42 | 866.4375 | -75
1 | 868.7875 | -36 | 866.4375 | -85
1 | 868.7875 | -41 | 866.4375 | -84
1 | 868.7875 | -41 | 866.4375 | -81
1 | 868.7875 | -40 | 866.4375 | -81
1 | 868.7875 | -30 | 866.4375 | -80
1 | 868.7875 | -36 | 866.4375 | -85
1 | 868.7875 | -38 | 866.4375 | -78
1 | 868.7875 | -40 | 866.4375 | -87
1 | 868.7875 | -37 | 866.4375 | -78
1 | 868.7875 | -38 | 866.4375 | -78
1 | 868.7875 | -41 | 866.4375 | -73
1 | 868.7875 | -41 | 866.4375 | -75
1 | 868.7875 | -50 | 866.4375 | -80
1 | 868.7875 | -41 | 866.4375 | -77
1 | 868.7875 | -38 | 866.4375 | -75
1 | 868.7875 | -37 | 866.4375 | -77
1 | 868.7875 | -38 | 866.4375 | -75
1 | 868.7875 | -44 | 866.4375 | -78
1 | 868.7875 | -37 | 866.4375 | -72
1 | 868.7875 | -50 | 866.4375 | -77
1 | 868.7875 | -38 | 866.4375 | -85
1 | 868.7875 | -38 | 866.4375 | -81
1 | 868.7875 | -45 | 866.4375 | -81
1 | 868.7875 | -42 | 866.4375 | -87
1 | 868.7875 | -47 | 866.4375 | -80
1 | 868.7875 | -41 | 866.4375 | -75
1 | 868.7875 | -42 | 866.4375 | -75
1 | 868.7875 | -48 | 866.4375 | -79
1 | 868.7875 | -40 | 866.4375 | -82
1 | 868.7875 | -44 | 866.4375 | -85
1 | 868.7875 | -45 | 866.4375 | -77
1 | 868.7875 | -40 | 866.4375 | -81
1 | 868.7875 | -41 | 866.4375 | -85
1 | 868.7875 | -34 | 866.4375 | -87
1 | 868.7875 | -46 | 866.4375 | -80
1 | 868.7875 | -52 | 866.4375 | -85
1 | 868.7875 | -56 | 866.4375 | -73
1 | 868.7875 | -48 | 866.4375 | -78
1 | 868.7875 | -40 | 866.4375 | -79
1 | 868.7875 | -46 | 866.4375 | -82
1 | 868.7875 | -51 | 866.4375 | -81
1 | 868.7875 | -44 | 866.4375 | -86
1 | 868.7875 | -37 | 866.4375 | -76
1 | 868.7875 | -38 | 866.4375 | -81
1 | 868.7875 | -40 | 866.4375 | -84
1 | 868.7875 | -42 | 866.4375 | -92
1 | 868.7875 | -39 | 866.4375 | -82
1 | 868.7875 | -42 | 866.4375 | -75
1 | 868.7875 | -39 | 866.4375 | -92
1 | 868.7875 | -41 | 866.4375 | -94
1 | 868.7875 | -36 | 866.4375 | -88
1 | 868.7875 | -37 | 866.4375 | -76
1 | 868.7875 | -41 | 866.4375 | -78
1 | 868.7875 | -45 | 866.4375 | -79
1 | 868.7875 | -42 | 866.4375 | -72
1 | 868.7875 | -42 | 866.4375 | -81
1 | 868.7875 | -36 | 866.4375 | -84
1 | 868.7875 | -42 | 866.4375 | -86
1 | 868.7875 | -39 | 866.4375 | -77
1 | 868.7875 | -43 | 866.4375 | -75
1 | 868.7875 | -41 | 866.4375 | -77
1 | 868.7875 | -42 | 866.4375 | -77
1 | 868.7875 | -42 | 866.4375 | -73
1 | 868.7875 | -42 | 866.4375 | -76
1 | 868.7875 | -44 | 866.4375 | -69
1 | 868.7875 | -44 | 866.4375 | -74
1 | 868.7875 | -42 | 866.4375 | -76
1 | 868.7875 | -58 | 866.4375 | -69
1 | 868.7875 | -48 | 866.4375 | -65
1 | 868.7875 | -50 | 866.4375 | -68
1 | 868.7875 | -41 | 866.4375 | -67
1 | 868.7875 | -43 | 866.4375 | -68
1 | 868.7875 | -49 | 866.4375 | -78
1 | 868.7875 | -53 | 866.4375 | -69
1 | 868.7875 | -46 | 866.4375 | -72
1 | 868.7875 | -48 | 866.4375 | -70
1 | 868.7875 | -48 | 866.4375 | -75
1 | 868.7875 | -47 | 866.4375 | -71
1 | 868.7875 | -40 | 866.4375 | -74
1 | 868.7875 | -40 | 866.4375 | -77
1 | 868.7875 | -52 | 866.4375 | -80
1 | 868.7875 | -50 | 866.4375 | -84
1 | 868.7875 | -40 | 866.4375 | -76
1 | 868.7875 | -44 | 866.4375 | -85
1 | 868.7875 | -48 | 866.4375 | -80
1 | 868.7875 | -45 | 866.4375 | -76
1 | 868.7875 | -54 | 866.4375 | -87
1 | 868.7875 | -62 | 866.4375 | -77
1 | 868.7875 | -47 | 866.4375 | -79
1 | 868.7875 | -48 | 866.4375 | -81
1 | 868.7875 | -39 | 866.4375 | -76
1 | 868.7875 | -54 | 866.4375 | -75
1 | 868.7875 | -71 | 866.4375 | -90
1 | 868.7875 | -52 | 866.4375 | -77
1 | 868.7875 | -54 | 866.4375 | -82
1 | 868.7875 | -42 | 866.4375 | -79
1 | 868.7875 | -47 | 866.4375 | -75
1 | 868.7875 | -44 | 866.4375 | -70
1 | 868.7875 | -45 | 866.4375 | -82
1 | 868.7875 | -55 | 866.4375 | -78
1 | 868.7875 | -50 | 866.4375 | -75
1 | 868.7875 | -46 | 866.4375 | -76
1 | 868.7875 | -45 | 866.4375 | -77
1 | 868.7875 | -43 | 866.4375 | -77
1 | 868.7875 | -40 | 866.4375 | -75
1 | 868.7875 | -45 | 866.4375 | -73
1 | 868.7875 | -44 | 866.4375 | -77
1 | 868.7875 | -43 | 866.4375 | -74
1 | 868.7875 | -53 | 866.4375 | -92
1 | 868.7875 | -40 | 866.4375 | -78
1 | 868.7875 | -42 | 866.4375 | -72
1 | 868.7875 | -50 | 866.4375 | -78
1 | 868.7875 | -48 | 866.4375 | -75
1 | 868.7875 | -55 | 866.4375 | -71
1 | 868.7875 | -43 | 866.4375 | -91
1 | 868.7875 | -48 | 866.4375 | -83
1 | 868.7875 | -47 | 866.4375 | -77
1 | 868.7875 | -48 | 866.4375 | -77
1 | 868.7875 | -47 | 866.4375 | -85
1 | 868.7875 | -52 | 866.4375 | -84
1 | 868.7875 | -48 | 866.4375 | -79
1 | 868.7875 | -42 | 866.4375 | -77
1 | 868.7875 | -57 | 866.4375 | -71
1 | 868.7875 | -53 | 866.4375 | -81
1 | 868.7875 | -44 | 866.4375 | -76
1 | 868.7875 | -61 | 866.4375 | -69
1 | 868.7875 | -51 | 866.4375 | -70
1 | 868.7875 | -46 | 866.4375 | -73
1 | 868.7875 | -44 | 866.4375 | -76
1 | 868.7875 | -47 | 866.4375 | -80
1 | 868.7875 | -43 | 866.4375 | -75
1 | 868.7875 | -58 | 866.4375 | -76
1 | 868.7875 | -49 | 866.4375 | -73
1 | 868.7875 | -47 | 866.4375 | -78
1 | 868.7875 | -47 | 866.4375 | -75
1 | 868.7875 | -48 | 866.4375 | -81
1 | 868.7875 | -51 | 866.4375 | -75
1 | 868.7875 | -53 | 866.4375 | -71
1 | 868.7875 | -51 | 866.4375 | -75
1 | 868.7875 | -50 | 866.4375 | -83
1 | 868.7875 | -46 | 866.4375 | -75
1 | 868.7875 | -51 | 866.4375 | -74
1 | 868.7875 | -46 | 866.4375 | -78
1 | 868.7875 | -45 | 866.4375 | -74
1 | 868.7875 | -62 | 866.4375 | -81
1 | 868.7875 | -45 | 866.4375 | -82
1 | 868.7875 | -63 | 866.4375 | -76
1 | 868.7875 | -51 | 866.4375 | -83
1 | 868.7875 | -63 | 866.4375 | -82
1 | 868.7875 | -51 | 866.4375 | -78
1 | 868.7875 | -60 | 866.4375 | -84
1 | 868.7875 | -77 | 866.4375 | -78
1 | 868.7875 | -75 | 866.4375 | -70
1 | 868.7875 | -47 | 866.4375 | -81
1 | 868.7875 | -55 | 866.4375 | -75
1 | 868.7875 | -48 | 866.4375 | -76
1 | 868.7875 | -60 | 866.4375 | -81
1 | 868.7875 | -74 | 866.4375 | -85
1 | 868.7875 | -44 | 866.4375 | -79
1 | 868.7875 | -46 | 866.4375 | -83
1 | 868.7875 | -52 | 866.4375 | -94
1 | 868.7875 | -52 | 866.4375 | -83
1 | 868.7875 | -51 | 866.4375 | -74
1 | 868.7875 | -53 | 866.4375 | -77
1 | 868.7875 | -81 | 866.4375 | -120
1 | 868.7875 | -78 | 866.4375 | -120
2 | 868.7875 | -80 | 866.4375 | -120
2 | 868.7875 | -80 | 866.4375 | -120
2 | 868.7875 | -97 | 866.4375 | -119
2 | 868.7875 | -96 | 866.4375 | -120
2 | 868.7875 | -81 | 866.4375 | -115
2 | 868.7875 | -80 | 866.4375 | -114
2 | 868.7875 | -86 | 866.4375 | -111
2 | 868.7875 | -81 | 866.4375 | -112
2 | 868.7875 | -79 | 866.4375 | -115
2 | 868.7875 | -78 | 866.4375 | -114
2 | 868.7875 | -80 | 866.4375 | -120
2 | 868.7875 | -77 | 866.4375 | -119
2 | 868.7875 | -81 | 866.4375 | -120
2 | 868.7875 | -91 | 866.4375 | -120
2 | 868.7875 | -93 | 866.4375 | -119
2 | 868.7875 | -89 | 866.4375 | -120
2 | 868.7875 | -89 | 866.4375 | -120
2 | 868.7875 | -109 | 866.4375 | -120
2 | 868.7875 | -91 | 866.4375 | -120
2 | 868.7875 | -103 | 866.4375 | -119
2 | 868.7875 | -95 | 866.4375 | -120
2 | 868.7875 | -92 | 866.4375 | -120
2 | 868.7875 | -96 | 866.4375 | -120
2 | 868.7875 | -86 | 866.4375 | -120
2 | 868.7875 | -90 | 866.4375 | -120
2 | 868.7875 | -103 | 866.4375 | -118
2 | 868.7875 | -91 | 866.4375 | -120
2 | 868.7875 | -91 | 866.4375 | -119
2 | 868.7875 | -106 | 866.4375 | -120
2 | 868.7875 | -85 | 866.4375 | -120
2 | 868.7875 | -92 | 866.4375 | -120
2 | 868.7875 | -91 | 866.4375 | -120
2 | 868.7875 | -96 | 866.4375 | -120
2 | 868.7875 | -92 | 866.4375 | -120
2 | 868.7875 | -89 | 866.4375 | -116
2 | 868.7875 | -97 | 866.4375 | -120
2 | 868.7875 | -93 | 866.4375 | -120
2 | 868.7875 | -94 | 866.4375 | -116
2 | 868.7875 | -112 | 866.4375 | -120
2 | 868.7875 | -95 | 866.4375 | -120
2 | 868.7875 | -92 | 866.4375 | -116
2 | 868.7875 | -88 | 866.4375 | -120
2 | 868.7875 | -97 | 866.4375 | -120
2 | 868.7875 | -93 | 866.4375 | -120
2 | 868.7875 | -91 | 866.4375 | -120
2 | 868.7875 | -95 | 866.4375 | -120
2 | 868.7875 | -97 | 866.4375 | -120
2 | 868.7875 | -98 | 866.4375 | -120
2 | 868.7875 | -97 | 866.4375 | -117
2 | 868.7875 | -103 | 866.4375 | -120
2 | 868.7875 | -100 | 866.4375 | -113
2 | 868.7875 | -93 | 866.4375 | -118
2 | 868.7875 | -88 | 866.4375 | -120
2 | 868.7875 | -89 | 866.4375 | -119
2 | 868.7875 | -84 | 866.4375 | -120
2 | 868.7875 | -88 | 866.4375 | -120
2 | 868.7875 | -100 | 866.4375 | -120
2 | 868.7875 | -92 | 866.4375 | -119
2 | 868.7875 | -92 | 866.4375 | -118
2 | 868.7875 | -93 | 866.4375 | -120
2 | 868.7875 | -93 | 866.4375 | -120
2 | 868.7875 | -86 | 866.4375 | -120
2 | 868.7875 | -85 | 866.4375 | -120
2 | 868.7875 | -85 | 866.4375 | -120
2 | 868.7875 | -81 | 866.4375 | -119
2 | 868.7875 | -92 | 866.4375 | -112
2 | 868.7875 | -80 | 866.4375 | -119
2 | 868.7875 | -100 | 866.4375 | -120
2 | 868.7875 | -93 | 866.4375 | -112
2 | 868.7875 | -78 | 866.4375 | -113
2 | 868.7875 | -81 | 866.4375 | -119
2 | 868.7875 | -84 | 866.4375 | -109
2 | 868.7875 | -83 | 866.4375 | -106
2 | 868.7875 | -84 | 866.4375 | -117
2 | 868.7875 | -79 | 866.4375 | -109
2 | 868.7875 | -94 | 866.4375 | -105
2 | 868.7875 | -77 | 866.4375 | -120
2 | 868.7875 | -87 | 866.4375 | -109
2 | 868.7875 | -89 | 866.4375 | -117
2 | 868.7875 | -79 | 866.4375 | -116
2 | 868.7875 | -83 | 866.4375 | -111
2 | 868.7875 | -94 | 866.4375 | -110
2 | 868.7875 | -78 | 866.4375 | -109
2 | 868.7875 | -84 | 866.4375 | -107
2 | 868.7875 | -92 | 866.4375 | -112
2 | 868.7875 | -83 | 866.4375 | -112
2 | 868.7875 | -102 | 866.4375 | -112
2 | 868.7875 | -91 | 866.4375 | -113
2 | 868.7875 | -95 | 866.4375 | -115
2 | 868.7875 | -84 | 866.4375 | -118
2 | 868.7875 | -86 | 866.4375 | -117
2 | 868.7875 | -88 | 866.4375 | -107
2 | 868.7875 | -89 | 866.4375 | -113
2 | 868.7875 | -83 | 866.4375 | -107
2 | 868.7875 | -81 | 866.4375 | -109
2 | 868.7875 | -81 | 866.4375 | -111
2 | 868.7875 | -89 | 866.4375 | -120
2 | 868.7875 | -84 | 866.4375 | -107
2 | 868.7875 | -78 | 866.4375 | -115
2 | 868.7875 | -85 | 866.4375 | -102
2 | 868.7875 | -85 | 866.4375 | -116
2 | 868.7875 | -89 | 866.4375 | -113
2 | 868.7875 | -85 | 866.4375 | -114
2 | 868.7875 | -81 | 866.4375 | -107
2 | 868.7875 | -90 | 866.4375 | -105
2 | 868.7875 | -82 | 866.4375 | -119
2 | 868.7875 | -91 | 866.4375 | -108
2 | 868.7875 | -83 | 866.4375 | -113
2 | 868.7875 | -87 | 866.4375 | -108
2 | 868.7875 | -92 | 866.4375 | -105
2 | 868.7875 | -90 | 866.4375 | -108
2 | 868.7875 | -103 | 866.4375 | -113
2 | 868.7875 | -77 | 866.4375 | -109
2 | 868.7875 | -79 | 866.4375 | -111
2 | 868.7875 | -89 | 866.4375 | -105
2 | 868.7875 | -80 | 866.4375 | -112
2 | 868.7875 | -88 | 866.4375 | -115
2 | 868.7875 | -90 | 866.4375 | -117
2 | 868.7875 | -97 | 866.4375 | -116
2 | 868.7875 | -86 | 866.4375 | -115
2 | 868.7875 | -82 | 866.4375 | -120
2 | 868.7875 | -79 | 866.4375 | -119
2 | 868.7875 | -80 | 866.4375 | -104
2 | 868.7875 | -95 | 866.4375 | -107
2 | 868.7875 | -86 | 866.4375 | -106
2 | 868.7875 | -96 | 866.4375 | -109
2 | 868.7875 | -80 | 866.4375 | -103
2 | 868.7875 | -81 | 866.4375 | -107
2 | 868.7875 | -99 | 866.4375 | -118
2 | 868.7875 | -83 | 866.4375 | -104
2 | 868.7875 | -84 | 866.4375 | -120
2 | 868.7875 | -90 | 866.4375 | -111
2 | 868.7875 | -89 | 866.4375 | -108
2 | 868.7875 | -86 | 866.4375 | -106
2 | 868.7875 | -88 | 866.4375 | -102
2 | 868.7875 | -87 | 866.4375 | -117
2 | 868.7875 | -90 | 866.4375 | -107
2 | 868.7875 | -81 | 866.4375 | -115
2 | 868.7875 | -82 | 866.4375 | -108
2 | 868.7875 | -98 | 866.4375 | -109
2 | 868.7875 | -81 | 866.4375 | -119
2 | 868.7875 | -81 | 866.4375 | -107
2 | 868.7875 | -96 | 866.4375 | -108
2 | 868.7875 | -84 | 866.4375 | -106
2 | 868.7875 | -94 | 866.4375 | -105
2 | 868.7875 | -88 | 866.4375 | -107
2 | 868.7875 | -82 | 866.4375 | -114
2 | 868.7875 | -85 | 866.4375 | -109
2 | 868.7875 | -79 | 866.4375 | -110
2 | 868.7875 | -86 | 866.4375 | -108
2 | 868.7875 | -90 | 866.4375 | -111
2 | 868.7875 | -77 | 866.4375 | -117
2 | 868.7875 | -89 | 866.4375 | -109
2 | 868.7875 | -81 | 866.4375 | -109
2 | 868.7875 | -87 | 866.4375 | -102
2 | 868.7875 | -92 | 866.4375 | -111
2 | 868.7875 | -82 | 866.4375 | -115
2 | 868.7875 | -84 | 866.4375 | -117
2 | 868.7875 | -87 | 866.4375 | -109
2 | 868.7875 | -94 | 866.4375 | -118
2 | 868.7875 | -89 | 866.4375 | -118
2 | 868.7875 | -85 | 866.4375 | -116
2 | 868.7875 | -89 | 866.4375 | -109
2 | 868.7875 | -86 | 866.4375 | -119
2 | 868.7875 | -87 | 866.4375 | -120
2 | 868.7875 | -88 | 866.4375 | -112
2 | 868.7875 | -86 | 866.4375 | -115
2 | 868.7875 | -87 | 866.4375 | -105
2 | 868.7875 | -90 | 866.4375 | -119
2 | 868.7875 | -88 | 866.4375 | -110
2 | 868.7875 | -86 | 866.4375 | -119
2 | 868.7875 | -93 | 866.4375 | -115
2 | 868.7875 | -93 | 866.4375 | -120
2 | 868.7875 | -89 | 866.4375 | -107
2 | 868.7875 | -85 | 866.4375 | -112
2 | 868.7875 | -101 | 866.4375 | -109
2 | 868.7875 | -85 | 866.4375 | -111
2 | 868.7875 | -96 | 866.4375 | -111
2 | 868.7875 | -92 | 866.4375 | -108
2 | 868.7875 | -100 | 866.4375 | -110
2 | 868.7875 | -91 | 866.4375 | -115
2 | 868.7875 | -96 | 866.4375 | -117
2 | 868.7875 | -94 | 866.4375 | -111
2 | 868.7875 | -86 | 866.4375 | -111
2 | 868.7875 | -105 | 866.4375 | -111
2 | 868.7875 | -94 | 866.4375 | -115
2 | 868.7875 | -96 | 866.4375 | -116
2 | 868.7875 | -100 | 866.4375 | -114
2 | 868.7875 | -93 | 866.4375 | -113
2 | 868.7875 | -94 | 866.4375 | -120
2 | 868.7875 | -91 | 866.4375 | -116
2 | 868.7875 | -93 | 866.4375 | -120
2 | 868.7875 | -111 | 866.4375 | -114
2 | 868.7875 | -102 | 866.4375 | -114
2 | 868.7875 | -72 | 866.4375 | -99
2 | 868.7875 | -72 | 866.4375 | -99
2 | 868.7875 | -71 | 866.4375 | -118
3 | 868.7875 | -77 | 866.4375 | -99
3 | 868.7875 | -73 | 866.4375 | -106
3 | 868.7875 | -70 | 866.4375 | -98
3 | 868.7875 | -73 | 866.4375 | -97
3 | 868.7875 | -73 | 866.4375 | -104
3 | 868.7875 | -72 | 866.4375 | -97
3 | 868.7875 | -87 | 866.4375 | -99
3 | 868.7875 | -79 | 866.4375 | -101
3 | 868.7875 | -72 | 866.4375 | -120
3 | 868.7875 | -75 | 866.4375 | -106
3 | 868.7875 | -99 | 866.4375 | -101
3 | 868.7875 | -73 | 866.4375 | -96
3 | 868.7875 | -72 | 866.4375 | -102
3 | 868.7875 | -82 | 866.4375 | -108
3 | 868.7875 | -81 | 866.4375 | -107
3 | 868.7875 | -82 | 866.4375 | -98
3 | 868.7875 | -83 | 866.4375 | -98
3 | 868.7875 | -82 | 866.4375 | -98
3 | 868.7875 | -96 | 866.4375 | -118
4 | 868.7875 | -97 | 866.4375 | -120
4 | 868.7875 | -96 | 866.4375 | -119
4 | 868.7875 | -107 | 866.4375 | -113
4 | 868.7875 | -91 | 866.4375 | -119
4 | 868.7875 | -86 | 866.4375 | -116
4 | 868.7875 | -94 | 866.4375 | -119
4 | 868.7875 | -90 | 866.4375 | -118
4 | 868.7875 | -108 | 866.4375 | -118
4 | 868.7875 | -98 | 866.4375 | -115
4 | 868.7875 | -91 | 866.4375 | -115
4 | 868.7875 | -87 | 866.4375 | -117
4 | 868.7875 | -93 | 866.4375 | -113
4 | 868.7875 | -87 | 866.4375 | -113
4 | 868.7875 | -87 | 866.4375 | -115
4 | 868.7875 | -104 | 866.4375 | -112
4 | 868.7875 | -86 | 866.4375 | -110
4 | 868.7875 | -103 | 866.4375 | -108
4 | 868.7875 | -96 | 866.4375 | -109
4 | 868.7875 | -94 | 866.4375 | -115
4 | 868.7875 | -89 | 866.4375 | -113
4 | 868.7875 | -87 | 866.4375 | -110
4 | 868.7875 | -87 | 866.4375 | -114
4 | 868.7875 | -92 | 866.4375 | -115
4 | 868.7875 | -90 | 866.4375 | -110
4 | 868.7875 | -86 | 866.4375 | -120
4 | 868.7875 | -91 | 866.4375 | -108
4 | 868.7875 | -97 | 866.4375 | -111
4 | 868.7875 | -104 | 866.4375 | -108
4 | 868.7875 | -89 | 866.4375 | -109
4 | 868.7875 | -92 | 866.4375 | -111
4 | 868.7875 | -86 | 866.4375 | -115
4 | 868.7875 | -88 | 866.4375 | -116
4 | 868.7875 | -90 | 866.4375 | -118
4 | 868.7875 | -90 | 866.4375 | -113
4 | 868.7875 | -99 | 866.4375 | -110
4 | 868.7875 | -82 | 866.4375 | -110
4 | 868.7875 | -95 | 866.4375 | -117
4 | 868.7875 | -87 | 866.4375 | -120
4 | 868.7875 | -89 | 866.4375 | -118
4 | 868.7875 | -99 | 866.4375 | -114
4 | 868.7875 | -83 | 866.4375 | -113
4 | 868.7875 | -95 | 866.4375 | -114
4 | 868.7875 | -88 | 866.4375 | -107
4 | 868.7875 | -82 | 866.4375 | -106
4 | 868.7875 | -80 | 866.4375 | -100
4 | 868.7875 | -79 | 866.4375 | -97
4 | 868.7875 | -76 | 866.4375 | -98
4 | 868.7875 | -73 | 866.4375 | -98
4 | 868.7875 | -74 | 866.4375 | -100
4 | 868.7875 | -73 | 866.4375 | -101
4 | 868.7875 | -73 | 866.4375 | -98
4 | 868.7875 | -73 | 866.4375 | -95
5 | 868.7875 | -71 | 866.4375 | -102
5 | 868.7875 | -70 | 866.4375 | -99
5 | 868.7875 | -69 | 866.4375 | -96
5 | 868.7875 | -74 | 866.4375 | -102
5 | 868.7875 | -72 | 866.4375 | -104
5 | 868.7875 | -72 | 866.4375 | -112
5 | 868.7875 | -68 | 866.4375 | -104
5 | 868.7875 | -68 | 866.4375 | -103
5 | 868.7875 | -67 | 866.4375 | -96
5 | 868.7875 | -69 | 866.4375 | -100
5 | 868.7875 | -70 | 866.4375 | -95
5 | 868.7875 | -71 | 866.4375 | -93
5 | 868.7875 | -71 | 866.4375 | -96
5 | 868.7875 | -72 | 866.4375 | -89
5 | 868.7875 | -78 | 866.4375 | -88
5 | 868.7875 | -70 | 866.4375 | -92
5 | 868.7875 | -71 | 866.4375 | -86
5 | 868.7875 | -73 | 866.4375 | -93
5 | 868.7875 | -75 | 866.4375 | -89
5 | 868.7875 | -66 | 866.4375 | -98
5 | 868.7875 | -62 | 866.4375 | -90
5 | 868.7875 | -61 | 866.4375 | -101
5 | 868.7875 | -65 | 866.4375 | -98
5 | 868.7875 | -71 | 866.4375 | -88
5 | 868.7875 | -62 | 866.4375 | -89
5 | 868.7875 | -65 | 866.4375 | -102
5 | 868.7875 | -72 | 866.4375 | -98
5 | 868.7875 | -68 | 866.4375 | -89
5 | 868.7875 | -66 | 866.4375 | -100
5 | 868.7875 | -73 | 866.4375 | -91
5 | 868.7875 | -87 | 866.4375 | -89
5 | 868.7875 | -75 | 866.4375 | -91
5 | 868.7875 | -76 | 866.4375 | -96
5 | 868.7875 | -80 | 866.4375 | -113
5 | 868.7875 | -73 | 866.4375 | -96
5 | 868.7875 | -68 | 866.4375 | -93
5 | 868.7875 | -80 | 866.4375 | -96
5 | 868.7875 | -94 | 866.4375 | -97
5 | 868.7875 | -74 | 866.4375 | -94
5 | 868.7875 | -76 | 866.4375 | -98
5 | 868.7875 | -71 | 866.4375 | -105
5 | 868.7875 | -72 | 866.4375 | -106
5 | 868.7875 | -77 | 866.4375 | -100
5 | 868.7875 | -65 | 866.4375 | -102
5 | 868.7875 | -75 | 866.4375 | -95
5 | 868.7875 | -80 | 866.4375 | -98
5 | 868.7875 | -78 | 866.4375 | -101
5 | 868.7875 | -79 | 866.4375 | -107
5 | 868.7875 | -72 | 866.4375 | -111
5 | 868.7875 | -73 | 866.4375 | -93
5 | 868.7875 | -74 | 866.4375 | -97
5 | 868.7875 | -77 | 866.4375 | -97
5 | 868.7875 | -80 | 866.4375 | -99
5 | 868.7875 | -71 | 866.4375 | -103
5 | 868.7875 | -70 | 866.4375 | -105
5 | 868.7875 | -73 | 866.4375 | -95
5 | 868.7875 | -74 | 866.4375 | -100
5 | 868.7875 | -82 | 866.4375 | -109
5 | 868.7875 | -79 | 866.4375 | -95
5 | 868.7875 | -80 | 866.4375 | -95
5 | 868.7875 | -72 | 866.4375 | -105
5 | 868.7875 | -77 | 866.4375 | -97
5 | 868.7875 | -75 | 866.4375 | -107
5 | 868.7875 | -83 | 866.4375 | -103
5 | 868.7875 | -73 | 866.4375 | -95
5 | 868.7875 | -75 | 866.4375 | -107
5 | 868.7875 | -69 | 866.4375 | -97
5 | 868.7875 | -67 | 866.4375 | -96
5 | 868.7875 | -66 | 866.4375 | -101
5 | 868.7875 | -74 | 866.4375 | -99
5 | 868.7875 | -78 | 866.4375 | -87
5 | 868.7875 | -70 | 866.4375 | -85
5 | 868.7875 | -69 | 866.4375 | -86
5 | 868.7875 | -69 | 866.4375 | -88
5 | 868.7875 | -64 | 866.4375 | -87
5 | 868.7875 | -64 | 866.4375 | -93
5 | 868.7875 | -70 | 866.4375 | -85
5 | 868.7875 | -69 | 866.4375 | -88
5 | 868.7875 | -73 | 866.4375 | -105
5 | 868.7875 | -64 | 866.4375 | -94
5 | 868.7875 | -71 | 866.4375 | -85
5 | 868.7875 | -72 | 866.4375 | -89
5 | 868.7875 | -67 | 866.4375 | -96
5 | 868.7875 | -68 | 866.4375 | -101
5 | 868.7875 | -73 | 866.4375 | -84
5 | 868.7875 | -69 | 866.4375 | -93
5 | 868.7875 | -74 | 866.4375 | -91
5 | 868.7875 | -69 | 866.4375 | -89
5 | 868.7875 | -71 | 866.4375 | -96
5 | 868.7875 | -69 | 866.4375 | -96
5 | 868.7875 | -79 | 866.4375 | -95
5 | 868.7875 | -80 | 866.4375 | -98
5 | 868.7875 | -76 | 866.4375 | -98
5 | 868.7875 | -71 | 866.4375 | -90
5 | 868.7875 | -68 | 866.4375 | -95
5 | 868.7875 | -65 | 866.4375 | -96
5 | 868.7875 | -73 | 866.4375 | -103
5 | 868.7875 | -76 | 866.4375 | -95
5 | 868.7875 | -68 | 866.4375 | -110
5 | 868.7875 | -80 | 866.4375 | -106
5 | 868.7875 | -76 | 866.4375 | -92
5 | 868.7875 | -72 | 866.4375 | -94
5 | 868.7875 | -71 | 866.4375 | -99
5 | 868.7875 | -86 | 866.4375 | -101
5 | 868.7875 | -85 | 866.4375 | -97
5 | 868.7875 | -83 | 866.4375 | -112
5 | 868.7875 | -77 | 866.4375 | -99
5 | 868.7875 | -84 | 866.4375 | -94
5 | 868.7875 | -76 | 866.4375 | -93
5 | 868.7875 | -71 | 866.4375 | -98
5 | 868.7875 | -74 | 866.4375 | -98
5 | 868.7875 | -102 | 866.4375 | -94
5 | 868.7875 | -74 | 866.4375 | -112
5 | 868.7875 | -73 | 866.4375 | -105
5 | 868.7875 | -67 | 866.4375 | -95
5 | 868.7875 | -65 | 866.4375 | -94
5 | 868.7875 | -79 | 866.4375 | -101
5 | 868.7875 | -73 | 866.4375 | -100
5 | 868.7875 | -68 | 866.4375 | -102
5 | 868.7875 | -64 | 866.4375 | -96
5 | 868.7875 | -78 | 866.4375 | -112
5 | 868.7875 | -77 | 866.4375 | -110
5 | 868.7875 | -81 | 866.4375 | -106
5 | 868.7875 | -81 | 866.4375 | -103
5 | 868.7875 | -87 | 866.4375 | -103
6 | 868.7875 | -88 | 866.4375 | -102
6 | 868.7875 | -80 | 866.4375 | -112
6 | 868.7875 | -90 | 866.4375 | -112
6 | 868.7875 | -93 | 866.4375 | -120
6 | 868.7875 | -81 | 866.4375 | -110
6 | 868.7875 | -95 | 866.4375 | -119
6 | 868.7875 | -94 | 866.4375 | -108
6 | 868.7875 | -97 | 866.4375 | -110
6 | 868.7875 | -84 | 866.4375 | -109
6 | 868.7875 | -76 | 866.4375 | -104
6 | 868.7875 | -77 | 866.4375 | -102
6 | 868.7875 | -83 | 866.4375 | -111
6 | 868.7875 | -81 | 866.4375 | -114
6 | 868.7875 | -93 | 866.4375 | -114
6 | 868.7875 | -85 | 866.4375 | -109
6 | 868.7875 | -85 | 866.4375 | -107
6 | 868.7875 | -101 | 866.4375 | -108
6 | 868.7875 | -83 | 866.4375 | -105
6 | 868.7875 | -78 | 866.4375 | -108
6 | 868.7875 | -75 | 866.4375 | -102
6 | 868.7875 | -81 | 866.4375 | -116
6 | 868.7875 | -84 | 866.4375 | -110
6 | 868.7875 | -81 | 866.4375 | -118
6 | 868.7875 | -81 | 866.4375 | -116
6 | 868.7875 | -79 | 866.4375 | -104
6 | 868.7875 | -90 | 866.4375 | -115
6 | 868.7875 | -83 | 866.4375 | -109
6 | 868.7875 | -77 | 866.4375 | -117
6 | 868.7875 | -77 | 866.4375 | -102
6 | 868.7875 | -80 | 866.4375 | -108
6 | 868.7875 | -94 | 866.4375 | -106
6 | 868.7875 | -77 | 866.4375 | -116
6 | 868.7875 | -84 | 866.4375 | -110
6 | 868.7875 | -76 | 866.4375 | -107
6 | 868.7875 | -86 | 866.4375 | -109
6 | 868.7875 | -79 | 866.4375 | -118
6 | 868.7875 | -88 | 866.4375 | -116
6 | 868.7875 | -82 | 866.4375 | -107
6 | 868.7875 | -82 | 866.4375 | -113
6 | 868.7875 | -92 | 866.4375 | -112
6 | 868.7875 | -75 | 866.4375 | -113
6 | 868.7875 | -93 | 866.4375 | -104
6 | 868.7875 | -74 | 866.4375 | -106
6 | 868.7875 | -79 | 866.4375 | -104
6 | 868.7875 | -87 | 866.4375 | -111
6 | 868.7875 | -75 | 866.4375 | -101
6 | 868.7875 | -72 | 866.4375 | -107
6 | 868.7875 | -82 | 866.4375 | -115
6 | 868.7875 | -81 | 866.4375 | -113
6 | 868.7875 | -76 | 866.4375 | -111
6 | 868.7875 | -71 | 866.4375 | -105
6 | 868.7875 | -79 | 866.4375 | -105
6 | 868.7875 | -75 | 866.4375 | -105
6 | 868.7875 | -74 | 866.4375 | -107
6 | 868.7875 | -79 | 866.4375 | -114
6 | 868.7875 | -76 | 866.4375 | -120
6 | 868.7875 | -79 | 866.4375 | -104
6 | 868.7875 | -71 | 866.4375 | -109
6 | 868.7875 | -69 | 866.4375 | -106
6 | 868.7875 | -71 | 866.4375 | -110
6 | 868.7875 | -68 | 866.4375 | -120
6 | 868.7875 | -75 | 866.4375 | -110
6 | 868.7875 | -68 | 866.4375 | -106
6 | 868.7875 | -84 | 866.4375 | -118
6 | 868.7875 | -78 | 866.4375 | -107
6 | 868.7875 | -72 | 866.4375 | -112
6 | 868.7875 | -67 | 866.4375 | -117
6 | 868.7875 | -68 | 866.4375 | -114
6 | 868.7875 | -80 | 866.4375 | -114
6 | 868.7875 | -69 | 866.4375 | -108
6 | 868.7875 | -88 | 866.4375 | -109
6 | 868.7875 | -73 | 866.4375 | -118
6 | 868.7875 | -65 | 866.4375 | -120
6 | 868.7875 | -66 | 866.4375 | -110
6 | 868.7875 | -65 | 866.4375 | -120
6 | 868.7875 | -69 | 866.4375 | -115
6 | 868.7875 | -74 | 866.4375 | -117
6 | 868.7875 | -80 | 866.4375 | -113
6 | 868.7875 | -70 | 866.4375 | -112
6 | 868.7875 | -88 | 866.4375 | -120
6 | 868.7875 | -79 | 866.4375 | -111
6 | 868.7875 | -69 | 866.4375 | -118
6 | 868.7875 | -68 | 866.4375 | -117
6 | 868.7875 | -67 | 866.4375 | -111
6 | 868.7875 | -66 | 866.4375 | -109
6 | 868.7875 | -75 | 866.4375 | -117
6 | 868.7875 | -92 | 866.4375 | -108
6 | 868.7875 | -73 | 866.4375 | -108
6 | 868.7875 | -75 | 866.4375 | -120
6 | 868.7875 | -68 | 866.4375 | -112
6 | 868.7875 | -72 | 866.4375 | -116
6 | 868.7875 | -74 | 866.4375 | -113
6 | 868.7875 | -72 | 866.4375 | -107
6 | 868.7875 | -70 | 866.4375 | -108
6 | 868.7875 | -82 | 866.4375 | -111
6 | 868.7875 | -66 | 866.4375 | -116
6 | 868.7875 | -77 | 866.4375 | -110
6 | 868.7875 | -70 | 866.4375 | -115
6 | 868.7875 | -75 | 866.4375 | -106
6 | 868.7875 | -66 | 866.4375 | -108
6 | 868.7875 | -64 | 866.4375 | -112
6 | 868.7875 | -71 | 866.4375 | -112
6 | 868.7875 | -63 | 866.4375 | -108
6 | 868.7875 | -75 | 866.4375 | -112
6 | 868.7875 | -67 | 866.4375 | -109
6 | 868.7875 | -68 | 866.4375 | -112
6 | 868.7875 | -71 | 866.4375 | -102
6 | 868.7875 | -66 | 866.4375 | -107
6 | 868.7875 | -67 | 866.4375 | -105
6 | 868.7875 | -69 | 866.4375 | -108
6 | 868.7875 | -62 | 866.4375 | -111
6 | 868.7875 | -58 | 866.4375 | -100
6 | 868.7875 | -56 | 866.4375 | -103
6 | 868.7875 | -57 | 866.4375 | -111
6 | 868.7875 | -52 | 866.4375 | -102
6 | 868.7875 | -65 | 866.4375 | -107
6 | 868.7875 | -69 | 866.4375 | -100
6 | 868.7875 | -54 | 866.4375 | -110
6 | 868.7875 | -75 | 866.4375 | -99
6 | 868.7875 | -58 | 866.4375 | -116
6 | 868.7875 | -62 | 866.4375 | -113
6 | 868.7875 | -62 | 866.4375 | -102
6 | 868.7875 | -63 | 866.4375 | -103
6 | 868.7875 | -71 | 866.4375 | -120
6 | 868.7875 | -54 | 866.4375 | -105
6 | 868.7875 | -60 | 866.4375 | -103
6 | 868.7875 | -65 | 866.4375 | -109
6 | 868.7875 | -59 | 866.4375 | -109
6 | 868.7875 | -60 | 866.4375 | -109
6 | 868.7875 | -65 | 866.4375 | -106
6 | 868.7875 | -62 | 866.4375 | -109
6 | 868.7875 | -78 | 866.4375 | -109
6 | 868.7875 | -66 | 866.4375 | -108
6 | 868.7875 | -67 | 866.4375 | -102
6 | 868.7875 | -76 | 866.4375 | -103
6 | 868.7875 | -61 | 866.4375 | -101
6 | 868.7875 | -64 | 866.4375 | -112
6 | 868.7875 | -63 | 866.4375 | -113
6 | 868.7875 | -65 | 866.4375 | -110
6 | 868.7875 | -85 | 866.4375 | -103
6 | 868.7875 | -65 | 866.4375 | -103
6 | 868.7875 | -66 | 866.4375 | -114
6 | 868.7875 | -59 | 866.4375 | -105
6 | 868.7875 | -60 | 866.4375 | -102
6 | 868.7875 | -74 | 866.4375 | -113
6 | 868.7875 | -68 | 866.4375 | -110
6 | 868.7875 | -63 | 866.4375 | -104
6 | 868.7875 | -70 | 866.4375 | -114
6 | 868.7875 | -58 | 866.4375 | -112
6 | 868.7875 | -57 | 866.4375 | -115
6 | 868.7875 | -64 | 866.4375 | -108
6 | 868.7875 | -58 | 866.4375 | -104
6 | 868.7875 | -78 | 866.4375 | -105
6 | 868.7875 | -69 | 866.4375 | -110
6 | 868.7875 | -62 | 866.4375 | -111
6 | 868.7875 | -64 | 866.4375 | -107
6 | 868.7875 | -63 | 866.4375 | -110
6 | 868.7875 | -79 | 866.4375 | -112
6 | 868.7875 | -58 | 866.4375 | -109
6 | 868.7875 | -71 | 866.4375 | -108
6 | 868.7875 | -62 | 866.4375 | -113
6 | 868.7875 | -68 | 866.4375 | -114
6 | 868.7875 | -70 | 866.4375 | -113
6 | 868.7875 | -65 | 866.4375 | -106
6 | 868.7875 | -72 | 866.4375 | -103
6 | 868.7875 | -72 | 866.4375 | -100
6 | 868.7875 | -69 | 866.4375 | -109
6 | 868.7875 | -82 | 866.4375 | -114
6 | 868.7875 | -71 | 866.4375 | -108
6 | 868.7875 | -68 | 866.4375 | -112
6 | 868.7875 | -75 | 866.4375 | -110
6 | 868.7875 | -71 | 866.4375 | -114
6 | 868.7875 | -76 | 866.4375 | -111
6 | 868.7875 | -67 | 866.4375 | -117
6 | 868.7875 | -68 | 866.4375 | -107
6 | 868.7875 | -73 | 866.4375 | -112
6 | 868.7875 | -78 | 866.4375 | -116
6 | 868.7875 | -79 | 866.4375 | -114
6 | 868.7875 | -76 | 866.4375 | -120
6 | 868.7875 | -79 | 866.4375 | -115
6 | 868.7875 | -74 | 866.4375 | -114
6 | 868.7875 | -72 | 866.4375 | -113
6 | 868.7875 | -77 | 866.4375 | -108
6 | 868.7875 | -69 | 866.4375 | -112
6 | 868.7875 | -68 | 866.4375 | -112
6 | 868.7875 | -74 | 866.4375 | -107
6 | 868.7875 | -79 | 866.4375 | -107
6 | 868.7875 | -74 | 866.4375 | -107
6 | 868.7875 | -69 | 866.4375 | -102
6 | 868.7875 | -71 | 866.4375 | -108
7 | 868.7875 | -70 | 866.4375 | -102
7 | 868.7875 | -75 | 866.4375 | -95
7 | 868.7875 | -70 | 866.4375 | -91
7 | 868.7875 | -68 | 866.4375 | -92
7 | 868.7875 | -72 | 866.4375 | -96
7 | 868.7875 | -70 | 866.4375 | -98
7 | 868.7875 | -76 | 866.4375 | -94
7 | 868.7875 | -69 | 866.4375 | -95
7 | 868.7875 | -79 | 866.4375 | -120
7 | 868.7875 | -68 | 866.4375 | -100
7 | 868.7875 | -85 | 866.4375 | -118
7 | 868.7875 | -74 | 866.4375 | -101
7 | 868.7875 | -78 | 866.4375 | -105
7 | 868.7875 | -73 | 866.4375 | -96
7 | 868.7875 | -74 | 866.4375 | -103
7 | 868.7875 | -74 | 866.4375 | -98
7 | 868.7875 | -77 | 866.4375 | -118
7 | 868.7875 | -77 | 866.4375 | -96
7 | 868.7875 | -72 | 866.4375 | -98
7 | 868.7875 | -86 | 866.4375 | -97
7 | 868.7875 | -71 | 866.4375 | -99
7 | 868.7875 | -68 | 866.4375 | -99
7 | 868.7875 | -79 | 866.4375 | -95
7 | 868.7875 | -72 | 866.4375 | -96
7 | 868.7875 | -71 | 866.4375 | -99
7 | 868.7875 | -71 | 866.4375 | -104
7 | 868.7875 | -75 | 866.4375 | -107
7 | 868.7875 | -71 | 866.4375 | -105
7 | 868.7875 | -68 | 866.4375 | -99
7 | 868.7875 | -63 | 866.4375 | -116
7 | 868.7875 | -73 | 866.4375 | -106
7 | 868.7875 | -67 | 866.4375 | -105
7 | 868.7875 | -77 | 866.4375 | -101
7 | 868.7875 | -66 | 866.4375 | -95
7 | 868.7875 | -81 | 866.4375 | -104
7 | 868.7875 | -72 | 866.4375 | -93
7 | 868.7875 | -67 | 866.4375 | -108
7 | 868.7875 | -64 | 866.4375 | -97
7 | 868.7875 | -71 | 866.4375 | -111
7 | 868.7875 | -67 | 866.4375 | -99
7 | 868.7875 | -65 | 866.4375 | -97
7 | 868.7875 | -67 | 866.4375 | -101
7 | 868.7875 | -66 | 866.4375 | -107
7 | 868.7875 | -73 | 866.4375 | -110
7 | 868.7875 | -69 | 866.4375 | -96
7 | 868.7875 | -65 | 866.4375 | -114
7 | 868.7875 | -68 | 866.4375 | -92
7 | 868.7875 | -63 | 866.4375 | -96
7 | 868.7875 | -69 | 866.4375 | -92
7 | 868.7875 | -72 | 866.4375 | -88
7 | 868.7875 | -64 | 866.4375 | -100
7 | 868.7875 | -73 | 866.4375 | -94
7 | 868.7875 | -64 | 866.4375 | -101
7 | 868.7875 | -64 | 866.4375 | -96
7 | 868.7875 | -75 | 866.4375 | -97
7 | 868.7875 | -70 | 866.4375 | -100
7 | 868.7875 | -65 | 866.4375 | -94
7 | 868.7875 | -64 | 866.4375 | -99
7 | 868.7875 | -66 | 866.4375 | -96
7 | 868.7875 | -66 | 866.4375 | -108
7 | 868.7875 | -68 | 866.4375 | -103
7 | 868.7875 | -69 | 866.4375 | -108
7 | 868.7875 | -70 | 866.4375 | -93
7 | 868.7875 | -69 | 866.4375 | -98
7 | 868.7875 | -65 | 866.4375 | -98
7 | 868.7875 | -73 | 866.4375 | -120
7 | 868.7875 | -72 | 866.4375 | -98
7 | 868.7875 | -69 | 866.4375 | -98
7 | 868.7875 | -68 | 866.4375 | -106
7 | 868.7875 | -83 | 866.4375 | -96
7 | 868.7875 | -75 | 866.4375 | -100
7 | 868.7875 | -82 | 866.4375 | -109
7 | 868.7875 | -74 | 866.4375 | -102
7 | 868.7875 | -74 | 866.4375 | -98
7 | 868.7875 | -76 | 866.4375 | -106
7 | 868.7875 | -78 | 866.4375 | -104
7 | 868.7875 | -69 | 866.4375 | -101
7 | 868.7875 | -76 | 866.4375 | -100
7 | 868.7875 | -92 | 866.4375 | -112
7 | 868.7875 | -76 | 866.4375 | -109
7 | 868.7875 | -80 | 866.4375 | -108
7 | 868.7875 | -74 | 866.4375 | -115
7 | 868.7875 | -77 | 866.4375 | -108
7 | 868.7875 | -87 | 866.4375 | -113
7 | 868.7875 | -87 | 866.4375 | -108
7 | 868.7875 | -82 | 866.4375 | -111
7 | 868.7875 | -76 | 866.4375 | -111
7 | 868.7875 | -91 | 866.4375 | -99
7 | 868.7875 | -82 | 866.4375 | -103
7 | 868.7875 | -81 | 866.4375 | -101
7 | 868.7875 | -79 | 866.4375 | -109
7 | 868.7875 | -76 | 866.4375 | -99
7 | 868.7875 | -87 | 866.4375 | -119
7 | 868.7875 | -78 | 866.4375 | -118
7 | 868.7875 | -78 | 866.4375 | -111
7 | 868.7875 | -91 | 866.4375 | -108
7 | 868.7875 | -83 | 866.4375 | -106
7 | 868.7875 | -91 | 866.4375 | -110
7 | 868.7875 | -84 | 866.4375 | -103
7 | 868.7875 | -86 | 866.4375 | -107
7 | 868.7875 | -76 | 866.4375 | -108
7 | 868.7875 | -79 | 866.4375 | -115
7 | 868.7875 | -75 | 866.4375 | -102
7 | 868.7875 | -77 | 866.4375 | -102
7 | 868.7875 | -77 | 866.4375 | -106
7 | 868.7875 | -78 | 866.4375 | -105
7 | 868.7875 | -81 | 866.4375 | -99
7 | 868.7875 | -77 | 866.4375 | -99
7 | 868.7875 | -78 | 866.4375 | -113
7 | 868.7875 | -80 | 866.4375 | -110
7 | 868.7875 | -78 | 866.4375 | -112
7 | 868.7875 | -97 | 866.4375 | -105
7 | 868.7875 | -84 | 866.4375 | -103
7 | 868.7875 | -81 | 866.4375 | -108
7 | 868.7875 | -80 | 866.4375 | -113
7 | 868.7875 | -82 | 866.4375 | -111
7 | 868.7875 | -80 | 866.4375 | -114
7 | 868.7875 | -84 | 866.4375 | -116
7 | 868.7875 | -82 | 866.4375 | -119
7 | 868.7875 | -86 | 866.4375 | -104
7 | 868.7875 | -84 | 866.4375 | -108
7 | 868.7875 | -81 | 866.4375 | -113
7 | 868.7875 | -87 | 866.4375 | -105
7 | 868.7875 | -87 | 866.4375 | -102
7 | 868.7875 | -106 | 866.4375 | -106
7 | 868.7875 | -84 | 866.4375 | -110
7 | 868.7875 | -84 | 866.4375 | -115
7 | 868.7875 | -80 | 866.4375 | -116
7 | 868.7875 | -94 | 866.4375 | -109
7 | 868.7875 | -85 | 866.4375 | -109
7 | 868.7875 | -78 | 866.4375 | -107
7 | 868.7875 | -86 | 866.4375 | -118
7 | 868.7875 | -79 | 866.4375 | -107
7 | 868.7875 | -79 | 866.4375 | -110
7 | 868.7875 | -75 | 866.4375 | -103
7 | 868.7875 | -81 | 866.4375 | -104
7 | 868.7875 | -84 | 866.4375 | -100
7 | 868.7875 | -75 | 866.4375 | -107
7 | 868.7875 | -83 | 866.4375 | -111
7 | 868.7875 | -79 | 866.4375 | -103
7 | 868.7875 | -88 | 866.4375 | -108
7 | 868.7875 | -89 | 866.4375 | -106
7 | 868.7875 | -83 | 866.4375 | -107
7 | 868.7875 | -77 | 866.4375 | -108
7 | 868.7875 | -79 | 866.4375 | -108
7 | 868.7875 | -84 | 866.4375 | -111
7 | 868.7875 | -89 | 866.4375 | -110
7 | 868.7875 | -79 | 866.4375 | -109
7 | 868.7875 | -84 | 866.4375 | -106
7 | 868.7875 | -78 | 866.4375 | -115
7 | 868.7875 | -81 | 866.4375 | -115
7 | 868.7875 | -83 | 866.4375 | -106
7 | 868.7875 | -89 | 866.4375 | -116
7 | 868.7875 | -107 | 866.4375 | -113
7 | 868.7875 | -85 | 866.4375 | -109
7 | 868.7875 | -87 | 866.4375 | -115
7 | 868.7875 | -98 | 866.4375 | -107
7 | 868.7875 | -86 | 866.4375 | -101
7 | 868.7875 | -81 | 866.4375 | -106
7 | 868.7875 | -85 | 866.4375 | -103
7 | 868.7875 | -89 | 866.4375 | -107
7 | 868.7875 | -87 | 866.4375 | -113
7 | 868.7875 | -82 | 866.4375 | -106
7 | 868.7875 | -84 | 866.4375 | -109
7 | 868.7875 | -91 | 866.4375 | -106
7 | 868.7875 | -79 | 866.4375 | -111
7 | 868.7875 | -90 | 866.4375 | -110
7 | 868.7875 | -84 | 866.4375 | -119
7 | 868.7875 | -87 | 866.4375 | -105
7 | 868.7875 | -79 | 866.4375 | -114
7 | 868.7875 | -83 | 866.4375 | -106
7 | 868.7875 | -78 | 866.4375 | -112
7 | 868.7875 | -81 | 866.4375 | -101
7 | 868.7875 | -90 | 866.4375 | -108
7 | 868.7875 | -83 | 866.4375 | -111
7 | 868.7875 | -86 | 866.4375 | -109
7 | 868.7875 | -85 | 866.4375 | -100
7 | 868.7875 | -83 | 866.4375 | -103
7 | 868.7875 | -78 | 866.4375 | -104
7 | 868.7875 | -84 | 866.4375 | -99
7 | 868.7875 | -92 | 866.4375 | -108
7 | 868.7875 | -96 | 866.4375 | -97
7 | 868.7875 | -76 | 866.4375 | -97
7 | 868.7875 | -81 | 866.4375 | -106
7 | 868.7875 | -76 | 866.4375 | -107
7 | 868.7875 | -82 | 866.4375 | -99
7 | 868.7875 | -83 | 866.4375 | -102
7 | 868.7875 | -79 | 866.4375 | -106
7 | 868.7875 | -81 | 866.4375 | -102
7 | 868.7875 | -77 | 866.4375 | -103
7 | 868.7875 | -84 | 866.4375 | -103
7 | 868.7875 | -94 | 866.4375 | -105
7 | 868.7875 | -86 | 866.4375 | -111
7 | 868.7875 | -85 | 866.4375 | -107
7 | 868.7875 | -76 | 866.4375 | -108
7 | 868.7875 | -76 | 866.4375 | -113
7 | 868.7875 | -80 | 866.4375 | -107
7 | 868.7875 | -87 | 866.4375 | -103
7 | 868.7875 | -76 | 866.4375 | -108
7 | 868.7875 | -79 | 866.4375 | -106
7 | 868.7875 | -75 | 866.4375 | -106
7 | 868.7875 | -77 | 866.4375 | -108
7 | 868.7875 | -73 | 866.4375 | -101
7 | 868.7875 | -75 | 866.4375 | -100
7 | 868.7875 | -74 | 866.4375 | -100
7 | 868.7875 | -80 | 866.4375 | -104
7 | 868.7875 | -83 | 866.4375 | -101
7 | 868.7875 | -79 | 866.4375 | -96
7 | 868.7875 | -89 | 866.4375 | -99
7 | 868.7875 | -77 | 866.4375 | -106
7 | 868.7875 | -77 | 866.4375 | -104
7 | 868.7875 | -77 | 866.4375 | -107
8 | 868.7875 | -79 | 866.4375 | -105
8 | 868.7875 | -80 | 866.4375 | -106
8 | 868.7875 | -79 | 866.4375 | -109
8 | 868.7875 | -77 | 866.4375 | -108
8 | 868.7875 | -78 | 866.4375 | -109
8 | 868.7875 | -71 | 866.4375 | -110
8 | 868.7875 | -71 | 866.4375 | -111
8 | 868.7875 | -77 | 866.4375 | -115
8 | 868.7875 | -72 | 866.4375 | -106
8 | 868.7875 | -86 | 866.4375 | -106
8 | 868.7875 | -84 | 866.4375 | -105
8 | 868.7875 | -76 | 866.4375 | -114
8 | 868.7875 | -70 | 866.4375 | -107
8 | 868.7875 | -72 | 866.4375 | -105
8 | 868.7875 | -73 | 866.4375 | -108
8 | 868.7875 | -75 | 866.4375 | -108
8 | 868.7875 | -70 | 866.4375 | -103
8 | 868.7875 | -70 | 866.4375 | -99
8 | 868.7875 | -81 | 866.4375 | -99
8 | 868.7875 | -70 | 866.4375 | -97
8 | 868.7875 | -71 | 866.4375 | -99
8 | 868.7875 | -61 | 866.4375 | -100
8 | 868.7875 | -64 | 866.4375 | -95
8 | 868.7875 | -66 | 866.4375 | -97
8 | 868.7875 | -62 | 866.4375 | -103
8 | 868.7875 | -61 | 866.4375 | -101
8 | 868.7875 | -56 | 866.4375 | -94
8 | 868.7875 | -62 | 866.4375 | -94
8 | 868.7875 | -65 | 866.4375 | -98
8 | 868.7875 | -64 | 866.4375 | -98
8 | 868.7875 | -66 | 866.4375 | -94
8 | 868.7875 | -65 | 866.4375 | -94
8 | 868.7875 | -68 | 866.4375 | -100
8 | 868.7875 | -63 | 866.4375 | -91
8 | 868.7875 | -60 | 866.4375 | -93
8 | 868.7875 | -71 | 866.4375 | -94
8 | 868.7875 | -73 | 866.4375 | -94
8 | 868.7875 | -66 | 866.4375 | -95
8 | 868.7875 | -71 | 866.4375 | -106
8 | 868.7875 | -57 | 866.4375 | -99
8 | 868.7875 | -61 | 866.4375 | -101
8 | 868.7875 | -60 | 866.4375 | -93
8 | 868.7875 | -51 | 866.4375 | -99
8 | 868.7875 | -57 | 866.4375 | -98
8 | 868.7875 | -51 | 866.4375 | -88
8 | 868.7875 | -51 | 866.4375 | -93
8 | 868.7875 | -58 | 866.4375 | -88
8 | 868.7875 | -57 | 866.4375 | -95
8 | 868.7875 | -51 | 866.4375 | -95
8 | 868.7875 | -54 | 866.4375 | -90
8 | 868.7875 | -62 | 866.4375 | -89
8 | 868.7875 | -50 | 866.4375 | -88
8 | 868.7875 | -49 | 866.4375 | -89
8 | 868.7875 | -52 | 866.4375 | -87
8 | 868.7875 | -56 | 866.4375 | -89
8 | 868.7875 | -56 | 866.4375 | -90
8 | 868.7875 | -56 | 866.4375 | -88
8 | 868.7875 | -54 | 866.4375 | -86
8 | 868.7875 | -54 | 866.4375 | -86
8 | 868.7875 | -55 | 866.4375 | -83
8 | 868.7875 | -55 | 866.4375 | -84
8 | 868.7875 | -54 | 866.4375 | -83
8 | 868.7875 | -51 | 866.4375 | -85
8 | 868.7875 | -52 | 866.4375 | -87
8 | 868.7875 | -52 | 866.4375 | -86
8 | 868.7875 | -51 | 866.4375 | -86
8 | 868.7875 | -59 | 866.4375 | -91
8 | 868.7875 | -56 | 866.4375 | -93
8 | 868.7875 | -69 | 866.4375 | -94
9 | 868.7875 | -69 | 866.4375 | -91
9 | 868.7875 | -68 | 866.4375 | -90
9 | 868.7875 | -69 | 866.4375 | -99
9 | 868.7875 | -72 | 866.4375 | -93
9 | 868.7875 | -69 | 866.4375 | -98
9 | 868.7875 | -63 | 866.4375 | -88
9 | 868.7875 | -65 | 866.4375 | -95
9 | 868.7875 | -67 | 866.4375 | -95
9 | 868.7875 | -76 | 866.4375 | -96
9 | 868.7875 | -61 | 866.4375 | -101
9 | 868.7875 | -61 | 866.4375 | -97
9 | 868.7875 | -71 | 866.4375 | -96
9 | 868.7875 | -69 | 866.4375 | -106
9 | 868.7875 | -66 | 866.4375 | -96
9 | 868.7875 | -67 | 866.4375 | -101
9 | 868.7875 | -64 | 866.4375 | -98
9 | 868.7875 | -65 | 866.4375 | -102
9 | 868.7875 | -65 | 866.4375 | -96
9 | 868.7875 | -63 | 866.4375 | -98
9 | 868.7875 | -64 | 866.4375 | -95
9 | 868.7875 | -78 | 866.4375 | -101
9 | 868.7875 | -73 | 866.4375 | -94
9 | 868.7875 | -70 | 866.4375 | -97
9 | 868.7875 | -64 | 866.4375 | -97
9 | 868.7875 | -67 | 866.4375 | -93
9 | 868.7875 | -73 | 866.4375 | -94
9 | 868.7875 | -76 | 866.4375 | -98
9 | 868.7875 | -69 | 866.4375 | -114
9 | 868.7875 | -64 | 866.4375 | -92
9 | 868.7875 | -72 | 866.4375 | -100
9 | 868.7875 | -68 | 866.4375 | -99
9 | 868.7875 | -75 | 866.4375 | -103
9 | 868.7875 | -62 | 866.4375 | -89
9 | 868.7875 | -65 | 866.4375 | -97
9 | 868.7875 | -74 | 866.4375 | -98
9 | 868.7875 | -75 | 866.4375 | -100
9 | 868.7875 | -62 | 866.4375 | -97
9 | 868.7875 | -63 | 866.4375 | -98
9 | 868.7875 | -62 | 866.4375 | -98
9 | 868.7875 | -63 | 866.4375 | -97
9 | 868.7875 | -67 | 866.4375 | -92
9 | 868.7875 | -59 | 866.4375 | -100
9 | 868.7875 | -72 | 866.4375 | -90
9 | 868.7875 | -69 | 866.4375 | -86
9 | 868.7875 | -64 | 866.4375 | -92
9 | 868.7875 | -74 | 866.4375 | -95
9 | 868.7875 | -72 | 866.4375 | -90
9 | 868.7875 | -64 | 866.4375 | -93
9 | 868.7875 | -61 | 866.4375 | -88
9 | 868.7875 | -64 | 866.4375 | -103
9 | 868.7875 | -69 | 866.4375 | -103
9 | 868.7875 | -62 | 866.4375 | -107
9 | 868.7875 | -84 | 866.4375 | -100
9 | 868.7875 | -66 | 866.4375 | -95
9 | 868.7875 | -64 | 866.4375 | -97
9 | 868.7875 | -74 | 866.4375 | -95
9 | 868.7875 | -74 | 866.4375 | -102
9 | 868.7875 | -75 | 866.4375 | -97
9 | 868.7875 | -76 | 866.4375 | -100
9 | 868.7875 | -77 | 866.4375 | -120
9 | 868.7875 | -78 | 866.4375 | -100
9 | 868.7875 | -72 | 866.4375 | -100
9 | 868.7875 | -75 | 866.4375 | -108
9 | 868.7875 | -69 | 866.4375 | -97
9 | 868.7875 | -76 | 866.4375 | -111
9 | 868.7875 | -75 | 866.4375 | -107
9 | 868.7875 | -86 | 866.4375 | -100
9 | 868.7875 | -69 | 866.4375 | -98
9 | 868.7875 | -78 | 866.4375 | -96
9 | 868.7875 | -84 | 866.4375 | -104
9 | 868.7875 | -74 | 866.4375 | -101
9 | 868.7875 | -70 | 866.4375 | -107
9 | 868.7875 | -67 | 866.4375 | -101
9 | 868.7875 | -71 | 866.4375 | -98
9 | 868.7875 | -78 | 866.4375 | -101
9 | 868.7875 | -85 | 866.4375 | -94
9 | 868.7875 | -72 | 866.4375 | -115
9 | 868.7875 | -78 | 866.4375 | -103
9 | 868.7875 | -72 | 866.4375 | -105
9 | 868.7875 | -78 | 866.4375 | -98
9 | 868.7875 | -76 | 866.4375 | -101
9 | 868.7875 | -75 | 866.4375 | -102
9 | 868.7875 | -73 | 866.4375 | -104
9 | 868.7875 | -78 | 866.4375 | -108
9 | 868.7875 | -83 | 866.4375 | -108
9 | 868.7875 | -78 | 866.4375 | -103
9 | 868.7875 | -76 | 866.4375 | -111
9 | 868.7875 | -75 | 866.4375 | -110
9 | 868.7875 | -74 | 866.4375 | -102
9 | 868.7875 | -87 | 866.4375 | -112
9 | 868.7875 | -73 | 866.4375 | -107
9 | 868.7875 | -85 | 866.4375 | -103
9 | 868.7875 | -94 | 866.4375 | -104
9 | 868.7875 | -76 | 866.4375 | -102
9 | 868.7875 | -96 | 866.4375 | -103
9 | 868.7875 | -73 | 866.4375 | -97
9 | 868.7875 | -77 | 866.4375 | -103
9 | 868.7875 | -80 | 866.4375 | -104
9 | 868.7875 | -75 | 866.4375 | -105
9 | 868.7875 | -76 | 866.4375 | -107
9 | 868.7875 | -77 | 866.4375 | -97
9 | 868.7875 | -77 | 866.4375 | -97
9 | 868.7875 | -75 | 866.4375 | -99
9 | 868.7875 | -78 | 866.4375 | -105
9 | 868.7875 | -74 | 866.4375 | -102
9 | 868.7875 | -87 | 866.4375 | -101
9 | 868.7875 | -85 | 866.4375 | -110
9 | 868.7875 | -98 | 866.4375 | -101
9 | 868.7875 | -83 | 866.4375 | -99
9 | 868.7875 | -82 | 866.4375 | -108
9 | 868.7875 | -78 | 866.4375 | -101
9 | 868.7875 | -76 | 866.4375 | -106
9 | 868.7875 | -79 | 866.4375 | -98
9 | 868.7875 | -83 | 866.4375 | -99
9 | 868.7875 | -74 | 866.4375 | -103
9 | 868.7875 | -76 | 866.4375 | -99
9 | 868.7875 | -86 | 866.4375 | -98
9 | 868.7875 | -76 | 866.4375 | -98
9 | 868.7875 | -76 | 866.4375 | -95
9 | 868.7875 | -77 | 866.4375 | -115
9 | 868.7875 | -75 | 866.4375 | -102
9 | 868.7875 | -97 | 866.4375 | -100
9 | 868.7875 | -81 | 866.4375 | -99
9 | 868.7875 | -75 | 866.4375 | -119
9 | 868.7875 | -87 | 866.4375 | -101
9 | 868.7875 | -85 | 866.4375 | -107
9 | 868.7875 | -84 | 866.4375 | -120
9 | 868.7875 | -84 | 866.4375 | -110
9 | 868.7875 | -85 | 866.4375 | -120
9 | 868.7875 | -82 | 866.4375 | -113
9 | 868.7875 | -83 | 866.4375 | -106
9 | 868.7875 | -79 | 866.4375 | -106
9 | 868.7875 | -78 | 866.4375 | -105
9 | 868.7875 | -87 | 866.4375 | -111
9 | 868.7875 | -81 | 866.4375 | -107
9 | 868.7875 | -93 | 866.4375 | -105
9 | 868.7875 | -85 | 866.4375 | -108
9 | 868.7875 | -84 | 866.4375 | -109
9 | 868.7875 | -85 | 866.4375 | -112
9 | 868.7875 | -83 | 866.4375 | -100
9 | 868.7875 | -81 | 866.4375 | -103
9 | 868.7875 | -79 | 866.4375 | -109
9 | 868.7875 | -81 | 866.4375 | -114
9 | 868.7875 | -80 | 866.4375 | -103
9 | 868.7875 | -80 | 866.4375 | -104
9 | 868.7875 | -79 | 866.4375 | -110
9 | 868.7875 | -79 | 866.4375 | -120
9 | 868.7875 | -83 | 866.4375 | -106
9 | 868.7875 | -90 | 866.4375 | -104
9 | 868.7875 | -84 | 866.4375 | -108
9 | 868.7875 | -77 | 866.4375 | -101
9 | 868.7875 | -79 | 866.4375 | -113
9 | 868.7875 | -81 | 866.4375 | -104
9 | 868.7875 | -77 | 866.4375 | -114
9 | 868.7875 | -86 | 866.4375 | -109
9 | 868.7875 | -76 | 866.4375 | -113
9 | 868.7875 | -74 | 866.4375 | -106
9 | 868.7875 | -86 | 866.4375 | -109
9 | 868.7875 | -80 | 866.4375 | -105
9 | 868.7875 | -83 | 866.4375 | -112
9 | 868.7875 | -96 | 866.4375 | -105
9 | 868.7875 | -80 | 866.4375 | -107
9 | 868.7875 | -103 | 866.4375 | -120
9 | 868.7875 | -77 | 866.4375 | -109
9 | 868.7875 | -77 | 866.4375 | -110
9 | 868.7875 | -78 | 866.4375 | -102
9 | 868.7875 | -75 | 866.4375 | -102
9 | 868.7875 | -77 | 866.4375 | -120
9 | 868.7875 | -72 | 866.4375 | -107
9 | 868.7875 | -82 | 866.4375 | -107
9 | 868.7875 | -78 | 866.4375 | -114
9 | 868.7875 | -70 | 866.4375 | -107
9 | 868.7875 | -76 | 866.4375 | -109
9 | 868.7875 | -73 | 866.4375 | -112
9 | 868.7875 | -80 | 866.4375 | -99
9 | 868.7875 | -77 | 866.4375 | -105
9 | 868.7875 | -73 | 866.4375 | -110
9 | 868.7875 | -75 | 866.4375 | -103
9 | 868.7875 | -77 | 866.4375 | -108
9 | 868.7875 | -78 | 866.4375 | -101
9 | 868.7875 | -73 | 866.4375 | -106
9 | 868.7875 | -78 | 866.4375 | -117
9 | 868.7875 | -71 | 866.4375 | -113
9 | 868.7875 | -78 | 866.4375 | -99
9 | 868.7875 | -75 | 866.4375 | -105
9 | 868.7875 | -70 | 866.4375 | -105
9 | 868.7875 | -78 | 866.4375 | -106
9 | 868.7875 | -74 | 866.4375 | -106
9 | 868.7875 | -75 | 866.4375 | -96
9 | 868.7875 | -72 | 866.4375 | -103
9 | 868.7875 | -64 | 866.4375 | -101
9 | 868.7875 | -66 | 866.4375 | -101
9 | 868.7875 | -77 | 866.4375 | -99
9 | 868.7875 | -71 | 866.4375 | -97
9 | 868.7875 | -63 | 866.4375 | -107
9 | 868.7875 | -66 | 866.4375 | -106
9 | 868.7875 | -71 | 866.4375 | -103
9 | 868.7875 | -73 | 866.4375 | -98
9 | 868.7875 | -78 | 866.4375 | -96
9 | 868.7875 | -63 | 866.4375 | -105
9 | 868.7875 | -67 | 866.4375 | -95
9 | 868.7875 | -82 | 866.4375 | -95
9 | 868.7875 | -64 | 866.4375 | -100
9 | 868.7875 | -69 | 866.4375 | -105
9 | 868.7875 | -69 | 866.4375 | -100
9 | 868.7875 | -90 | 866.4375 | -104
9 | 868.7875 | -66 | 866.4375 | -105
9 | 868.7875 | -67 | 866.4375 | -102
9 | 868.7875 | -66 | 866.4375 | -106
9 | 868.7875 | -69 | 866.4375 | -102
9 | 868.7875 | -76 | 866.4375 | -101
9 | 868.7875 | -79 | 866.4375 | -97
9 | 868.7875 | -75 | 866.4375 | -103
9 | 868.7875 | -70 | 866.4375 | -103
9 | 868.7875 | -68 | 866.4375 | -96
9 | 868.7875 | -70 | 866.4375 | -93
9 | 868.7875 | -72 | 866.4375 | -101
9 | 868.7875 | -70 | 866.4375 | -96
9 | 868.7875 | -66 | 866.4375 | -95
9 | 868.7875 | -68 | 866.4375 | -104
9 | 868.7875 | -65 | 866.4375 | -98
9 | 868.7875 | -65 | 866.4375 | -97
9 | 868.7875 | -64 | 866.4375 | -91
9 | 868.7875 | -70 | 866.4375 | -107
9 | 868.7875 | -77 | 866.4375 | -102
9 | 868.7875 | -71 | 866.4375 | -101
9 | 868.7875 | -78 | 866.4375 | -102
9 | 868.7875 | -72 | 866.4375 | -93
9 | 868.7875 | -74 | 866.4375 | -96
9 | 868.7875 | -65 | 866.4375 | -95
9 | 868.7875 | -63 | 866.4375 | -91
9 | 868.7875 | -71 | 866.4375 | -91
9 | 868.7875 | -71 | 866.4375 | -92
9 | 868.7875 | -74 | 866.4375 | -90
9 | 868.7875 | -72 | 866.4375 | -90
9 | 868.7875 | -72 | 866.4375 | -94
9 | 868.7875 | -72 | 866.4375 | -94
9 | 868.7875 | -86 | 866.4375 | -110
9 | 868.7875 | -96 | 866.4375 | -104
10 | 868.7875 | -95 | 866.4375 | -101
10 | 868.7875 | -74 | 866.4375 | -101
10 | 868.7875 | -85 | 866.4375 | -99
10 | 868.7875 | -89 | 866.4375 | -109
10 | 868.7875 | -76 | 866.4375 | -106
10 | 868.7875 | -76 | 866.4375 | -114
10 | 868.7875 | -82 | 866.4375 | -100
10 | 868.7875 | -77 | 866.4375 | -119
10 | 868.7875 | -90 | 866.4375 | -102
10 | 868.7875 | -75 | 866.4375 | -104
10 | 868.7875 | -78 | 866.4375 | -103
10 | 868.7875 | -77 | 866.4375 | -105
10 | 868.7875 | -79 | 866.4375 | -111
10 | 868.7875 | -71 | 866.4375 | -116
10 | 868.7875 | -73 | 866.4375 | -105
10 | 868.7875 | -70 | 866.4375 | -108
10 | 868.7875 | -84 | 866.4375 | -114
10 | 868.7875 | -78 | 866.4375 | -105
10 | 868.7875 | -86 | 866.4375 | -120
10 | 868.7875 | -74 | 866.4375 | -120
10 | 868.7875 | -83 | 866.4375 | -117
10 | 868.7875 | -88 | 866.4375 | -100
10 | 868.7875 | -73 | 866.4375 | -111
10 | 868.7875 | -78 | 866.4375 | -100
10 | 868.7875 | -81 | 866.4375 | -96
10 | 868.7875 | -72 | 866.4375 | -109
10 | 868.7875 | -75 | 866.4375 | -99
10 | 868.7875 | -67 | 866.4375 | -107
10 | 868.7875 | -67 | 866.4375 | -102
10 | 868.7875 | -68 | 866.4375 | -96
10 | 868.7875 | -67 | 866.4375 | -98
10 | 868.7875 | -69 | 866.4375 | -101
10 | 868.7875 | -71 | 866.4375 | -111
10 | 868.7875 | -67 | 866.4375 | -99
10 | 868.7875 | -69 | 866.4375 | -101
10 | 868.7875 | -74 | 866.4375 | -110
10 | 868.7875 | -72 | 866.4375 | -105
10 | 868.7875 | -66 | 866.4375 | -107
10 | 868.7875 | -62 | 866.4375 | -99
10 | 868.7875 | -60 | 866.4375 | -108
10 | 868.7875 | -68 | 866.4375 | -104
10 | 868.7875 | -66 | 866.4375 | -109
10 | 868.7875 | -85 | 866.4375 | -112
10 | 868.7875 | -64 | 866.4375 | -101
10 | 868.7875 | -70 | 866.4375 | -106
10 | 868.7875 | -81 | 866.4375 | -104
10 | 868.7875 | -60 | 866.4375 | -105
10 | 868.7875 | -66 | 866.4375 | -105
10 | 868.7875 | -57 | 866.4375 | -103
10 | 868.7875 | -70 | 866.4375 | -95
10 | 868.7875 | -64 | 866.4375 | -102
10 | 868.7875 | -64 | 866.4375 | -97
10 | 868.7875 | -58 | 866.4375 | -96
10 | 868.7875 | -56 | 866.4375 | -99
10 | 868.7875 | -60 | 866.4375 | -99
10 | 868.7875 | -55 | 866.4375 | -95
10 | 868.7875 | -56 | 866.4375 | -104
10 | 868.7875 | -66 | 866.4375 | -104
10 | 868.7875 | -67 | 866.4375 | -99
10 | 868.7875 | -71 | 866.4375 | -114
10 | 868.7875 | -58 | 866.4375 | -96
10 | 868.7875 | -82 | 866.4375 | -115
10 | 868.7875 | -61 | 866.4375 | -108
10 | 868.7875 | -64 | 866.4375 | -117
10 | 868.7875 | -60 | 866.4375 | -100
10 | 868.7875 | -60 | 866.4375 | -103
10 | 868.7875 | -56 | 866.4375 | -99
10 | 868.7875 | -56 | 866.4375 | -105
10 | 868.7875 | -62 | 866.4375 | -98
10 | 868.7875 | -59 | 866.4375 | -105
10 | 868.7875 | -64 | 866.4375 | -104
10 | 868.7875 | -69 | 866.4375 | -98
10 | 868.7875 | -64 | 866.4375 | -102
10 | 868.7875 | -61 | 866.4375 | -106
10 | 868.7875 | -55 | 866.4375 | -110
10 | 868.7875 | -58 | 866.4375 | -99
10 | 868.7875 | -58 | 866.4375 | -102
10 | 868.7875 | -66 | 866.4375 | -95
10 | 868.7875 | -61 | 866.4375 | -95
10 | 868.7875 | -55 | 866.4375 | -112
10 | 868.7875 | -59 | 866.4375 | -108
10 | 868.7875 | -55 | 866.4375 | -112
10 | 868.7875 | -58 | 866.4375 | -107
10 | 868.7875 | -62 | 866.4375 | -104
10 | 868.7875 | -62 | 866.4375 | -96
10 | 868.7875 | -74 | 866.4375 | -109
10 | 868.7875 | -56 | 866.4375 | -109
10 | 868.7875 | -52 | 866.4375 | -98
10 | 868.7875 | -54 | 866.4375 | -104
10 | 868.7875 | -59 | 866.4375 | -94
10 | 868.7875 | -64 | 866.4375 | -96
10 | 868.7875 | -54 | 866.4375 | -111
10 | 868.7875 | -51 | 866.4375 | -105
10 | 868.7875 | -55 | 866.4375 | -102
10 | 868.7875 | -62 | 866.4375 | -109
10 | 868.7875 | -50 | 866.4375 | -96
10 | 868.7875 | -50 | 866.4375 | -103
10 | 868.7875 | -53 | 866.4375 | -100
10 | 868.7875 | -48 | 866.4375 | -102
10 | 868.7875 | -60 | 866.4375 | -99
10 | 868.7875 | -49 | 866.4375 | -100
10 | 868.7875 | -55 | 866.4375 | -105
10 | 868.7875 | -60 | 866.4375 | -108
10 | 868.7875 | -52 | 866.4375 | -110
10 | 868.7875 | -50 | 866.4375 | -98
10 | 868.7875 | -53 | 866.4375 | -115
10 | 868.7875 | -57 | 866.4375 | -101
10 | 868.7875 | -61 | 866.4375 | -103
10 | 868.7875 | -58 | 866.4375 | -102
10 | 868.7875 | -62 | 866.4375 | -101
10 | 868.7875 | -61 | 866.4375 | -99
10 | 868.7875 | -59 | 866.4375 | -96
10 | 868.7875 | -59 | 866.4375 | -102
10 | 868.7875 | -55 | 866.4375 | -101
10 | 868.7875 | -59 | 866.4375 | -111
10 | 868.7875 | -59 | 866.4375 | -111
10 | 868.7875 | -55 | 866.4375 | -106
10 | 868.7875 | -56 | 866.4375 | -96
10 | 868.7875 | -62 | 866.4375 | -103
10 | 868.7875 | -54 | 866.4375 | -109
10 | 868.7875 | -56 | 866.4375 | -118
10 | 868.7875 | -62 | 866.4375 | -107
10 | 868.7875 | -55 | 866.4375 | -107
10 | 868.7875 | -70 | 866.4375 | -105
10 | 868.7875 | -67 | 866.4375 | -104
10 | 868.7875 | -64 | 866.4375 | -107
10 | 868.7875 | -58 | 866.4375 | -107
10 | 868.7875 | -63 | 866.4375 | -106
10 | 868.7875 | -70 | 866.4375 | -110
10 | 868.7875 | -58 | 866.4375 | -108
10 | 868.7875 | -67 | 866.4375 | -119
10 | 868.7875 | -59 | 866.4375 | -112
10 | 868.7875 | -62 | 866.4375 | -101
10 | 868.7875 | -61 | 866.4375 | -107
10 | 868.7875 | -61 | 866.4375 | -103
10 | 868.7875 | -66 | 866.4375 | -104
10 | 868.7875 | -62 | 866.4375 | -113
10 | 868.7875 | -58 | 866.4375 | -107
10 | 868.7875 | -61 | 866.4375 | -117
10 | 868.7875 | -64 | 866.4375 | -107
10 | 868.7875 | -73 | 866.4375 | -109
10 | 868.7875 | -79 | 866.4375 | -107
10 | 868.7875 | -64 | 866.4375 | -112
10 | 868.7875 | -71 | 866.4375 | -112
10 | 868.7875 | -69 | 866.4375 | -99
10 | 868.7875 | -60 | 866.4375 | -118
10 | 868.7875 | -69 | 866.4375 | -101
10 | 868.7875 | -62 | 866.4375 | -101
10 | 868.7875 | -64 | 866.4375 | -112
10 | 868.7875 | -70 | 866.4375 | -105
10 | 868.7875 | -86 | 866.4375 | -103
10 | 868.7875 | -75 | 866.4375 | -104
10 | 868.7875 | -75 | 866.4375 | -103
10 | 868.7875 | -67 | 866.4375 | -116
10 | 868.7875 | -65 | 866.4375 | -103
10 | 868.7875 | -72 | 866.4375 | -106
10 | 868.7875 | -64 | 866.4375 | -107
10 | 868.7875 | -69 | 866.4375 | -102
10 | 868.7875 | -71 | 866.4375 | -109
10 | 868.7875 | -61 | 866.4375 | -108
10 | 868.7875 | -71 | 866.4375 | -103
10 | 868.7875 | -69 | 866.4375 | -110
10 | 868.7875 | -73 | 866.4375 | -118
10 | 868.7875 | -70 | 866.4375 | -102
10 | 868.7875 | -71 | 866.4375 | -107
10 | 868.7875 | -74 | 866.4375 | -97
10 | 868.7875 | -64 | 866.4375 | -100
10 | 868.7875 | -67 | 866.4375 | -102
10 | 868.7875 | -75 | 866.4375 | -105
10 | 868.7875 | -81 | 866.4375 | -106
10 | 868.7875 | -65 | 866.4375 | -95
10 | 868.7875 | -70 | 866.4375 | -99
10 | 868.7875 | -60 | 866.4375 | -107
10 | 868.7875 | -67 | 866.4375 | -107
10 | 868.7875 | -66 | 866.4375 | -103
10 | 868.7875 | -59 | 866.4375 | -92
10 | 868.7875 | -64 | 866.4375 | -105
10 | 868.7875 | -62 | 866.4375 | -108
10 | 868.7875 | -61 | 866.4375 | -105
10 | 868.7875 | -61 | 866.4375 | -98
10 | 868.7875 | -63 | 866.4375 | -103
10 | 868.7875 | -66 | 866.4375 | -98
10 | 868.7875 | -67 | 866.4375 | -109
10 | 868.7875 | -64 | 866.4375 | -97
10 | 868.7875 | -62 | 866.4375 | -92
10 | 868.7875 | -60 | 866.4375 | -110
10 | 868.7875 | -61 | 866.4375 | -92
10 | 868.7875 | -59 | 866.4375 | -100
10 | 868.7875 | -65 | 866.4375 | -96
10 | 868.7875 | -60 | 866.4375 | -99
10 | 868.7875 | -57 | 866.4375 | -111
10 | 868.7875 | -60 | 866.4375 | -97
10 | 868.7875 | -66 | 866.4375 | -102
10 | 868.7875 | -64 | 866.4375 | -99
10 | 868.7875 | -60 | 866.4375 | -95
10 | 868.7875 | -60 | 866.4375 | -96
10 | 868.7875 | -58 | 866.4375 | -89
10 | 868.7875 | -61 | 866.4375 | -90
10 | 868.7875 | -69 | 866.4375 | -99
10 | 868.7875 | -63 | 866.4375 | -103
10 | 868.7875 | -78 | 866.4375 | -97
10 | 868.7875 | -59 | 866.4375 | -95
10 | 868.7875 | -57 | 866.4375 | -98
10 | 868.7875 | -59 | 866.4375 | -87
10 | 868.7875 | -66 | 866.4375 | -87
10 | 868.7875 | -65 | 866.4375 | -87
10 | 868.7875 | -60 | 866.4375 | -87
10 | 868.7875 | -68 | 866.4375 | -85
10 | 868.7875 | -57 | 866.4375 | -85
10 | 868.7875 | -66 | 866.4375 | -84
10 | 868.7875 | -56 | 866.4375 | -80
10 | 868.7875 | -58 | 866.4375 | -86
10 | 868.7875 | -52 | 866.4375 | -91
10 | 868.7875 | -61 | 866.4375 | -110
10 | 868.7875 | -54 | 866.4375 | -93
10 | 868.7875 | -54 | 866.4375 | -100
10 | 868.7875 | -64 | 866.4375 | -90
10 | 868.7875 | -54 | 866.4375 | -89
10 | 868.7875 | -49 | 866.4375 | -89
10 | 868.7875 | -51 | 866.4375 | -91
10 | 868.7875 | -54 | 866.4375 | -87
10 | 868.7875 | -69 | 866.4375 | -84
10 | 868.7875 | -58 | 866.4375 | -87
10 | 868.7875 | -69 | 866.4375 | -84
10 | 868.7875 | -69 | 866.4375 | -83
10 | 868.7875 | -63 | 866.4375 | -85
10 | 868.7875 | -52 | 866.4375 | -85
11 | 868.7875 | -47 | 866.4375 | -82
11 | 868.7875 | -59 | 866.4375 | -104
11 | 868.7875 | -47 | 866.4375 | -103
11 | 868.7875 | -60 | 866.4375 | -83
11 | 868.7875 | -65 | 866.4375 | -112
11 | 868.7875 | -51 | 866.4375 | -86
11 | 868.7875 | -62 | 866.4375 | -86
11 | 868.7875 | -58 | 866.4375 | -89
11 | 868.7875 | -59 | 866.4375 | -88
11 | 868.7875 | -64 | 866.4375 | -87
11 | 868.7875 | -60 | 866.4375 | -86
11 | 868.7875 | -69 | 866.4375 | -88
11 | 868.7875 | -60 | 866.4375 | -83
11 | 868.7875 | -67 | 866.4375 | -87
11 | 868.7875 | -62 | 866.4375 | -92
11 | 868.7875 | -49 | 866.4375 | -92
11 | 868.7875 | -60 | 866.4375 | -91
11 | 868.7875 | -59 | 866.4375 | -102
11 | 868.7875 | -55 | 866.4375 | -85
11 | 868.7875 | -51 | 866.4375 | -87
11 | 868.7875 | -55 | 866.4375 | -83
11 | 868.7875 | -59 | 866.4375 | -90
11 | 868.7875 | -57 | 866.4375 | -90
11 | 868.7875 | -51 | 866.4375 | -90
11 | 868.7875 | -49 | 866.4375 | -91
11 | 868.7875 | -53 | 866.4375 | -88
11 | 868.7875 | -54 | 866.4375 | -94
11 | 868.7875 | -55 | 866.4375 | -88
11 | 868.7875 | -60 | 866.4375 | -85
11 | 868.7875 | -54 | 866.4375 | -89
11 | 868.7875 | -57 | 866.4375 | -85
11 | 868.7875 | -65 | 866.4375 | -81
11 | 868.7875 | -63 | 866.4375 | -83
11 | 868.7875 | -62 | 866.4375 | -93
11 | 868.7875 | -61 | 866.4375 | -91
11 | 868.7875 | -62 | 866.4375 | -93
11 | 868.7875 | -62 | 866.4375 | -96
11 | 868.7875 | -62 | 866.4375 | -95
11 | 868.7875 | -62 | 866.4375 | -88
11 | 868.7875 | -59 | 866.4375 | -89
11 | 868.7875 | -57 | 866.4375 | -93
11 | 868.7875 | -60 | 866.4375 | -94
11 | 868.7875 | -63 | 866.4375 | -95
11 | 868.7875 | -72 | 866.4375 | -107
11 | 868.7875 | -59 | 866.4375 | -98
11 | 868.7875 | -83 | 866.4375 | -92
11 | 868.7875 | -61 | 866.4375 | -114
11 | 868.7875 | -61 | 866.4375 | -100
11 | 868.7875 | -67 | 866.4375 | -97
11 | 868.7875 | -74 | 866.4375 | -109
11 | 868.7875 | -66 | 866.4375 | -107
11 | 868.7875 | -68 | 866.4375 | -95
11 | 868.7875 | -64 | 866.4375 | -99
11 | 868.7875 | -61 | 866.4375 | -90
11 | 868.7875 | -55 | 866.4375 | -91
11 | 868.7875 | -64 | 866.4375 | -89
11 | 868.7875 | -78 | 866.4375 | -99
11 | 868.7875 | -66 | 866.4375 | -96
11 | 868.7875 | -61 | 866.4375 | -94
11 | 868.7875 | -62 | 866.4375 | -93
11 | 868.7875 | -65 | 866.4375 | -97
11 | 868.7875 | -66 | 866.4375 | -95
11 | 868.7875 | -63 | 866.4375 | -98
11 | 868.7875 | -56 | 866.4375 | -102
11 | 868.7875 | -57 | 866.4375 | -90
11 | 868.7875 | -53 | 866.4375 | -90
11 | 868.7875 | -52 | 866.4375 | -87
11 | 868.7875 | -63 | 866.4375 | -91
11 | 868.7875 | -54 | 866.4375 | -91
11 | 868.7875 | -53 | 866.4375 | -92
11 | 868.7875 | -61 | 866.4375 | -93
11 | 868.7875 | -54 | 866.4375 | -90
11 | 868.7875 | -55 | 866.4375 | -93
11 | 868.7875 | -61 | 866.4375 | -104
11 | 868.7875 | -58 | 866.4375 | -103
11 | 868.7875 | -56 | 866.4375 | -89
11 | 868.7875 | -58 | 866.4375 | -105
11 | 868.7875 | -62 | 866.4375 | -107
11 | 868.7875 | -67 | 866.4375 | -102
11 | 868.7875 | -67 | 866.4375 | -97
11 | 868.7875 | -66 | 866.4375 | -95
11 | 868.7875 | -71 | 866.4375 | -104
11 | 868.7875 | -66 | 866.4375 | -94
11 | 868.7875 | -71 | 866.4375 | -104
11 | 868.7875 | -89 | 866.4375 | -105
11 | 868.7875 | -66 | 866.4375 | -107
11 | 868.7875 | -70 | 866.4375 | -108
11 | 868.7875 | -73 | 866.4375 | -120
11 | 868.7875 | -76 | 866.4375 | -109
11 | 868.7875 | -78 | 866.4375 | -103
11 | 868.7875 | -71 | 866.4375 | -102
11 | 868.7875 | -77 | 866.4375 | -108
11 | 868.7875 | -76 | 866.4375 | -104
11 | 868.7875 | -78 | 866.4375 | -108
11 | 868.7875 | -73 | 866.4375 | -106
11 | 868.7875 | -72 | 866.4375 | -105
11 | 868.7875 | -72 | 866.4375 | -111
11 | 868.7875 | -81 | 866.4375 | -115
11 | 868.7875 | -80 | 866.4375 | -120
11 | 868.7875 | -76 | 866.4375 | -110
11 | 868.7875 | -84 | 866.4375 | -109
11 | 868.7875 | -76 | 866.4375 | -109
11 | 868.7875 | -77 | 866.4375 | -112
11 | 868.7875 | -93 | 866.4375 | -116
11 | 868.7875 | -78 | 866.4375 | -111
11 | 868.7875 | -80 | 866.4375 | -117
11 | 868.7875 | -94 | 866.4375 | -105
11 | 868.7875 | -83 | 866.4375 | -117
11 | 868.7875 | -77 | 866.4375 | -110
11 | 868.7875 | -85 | 866.4375 | -109