## Data
CRITICAL ONE BUILDINGS | [15 empty] | Predicted ITAC Coverage (-97 dBm) |  |  |  | Tested for P25 (-105 dBm)
Building_Name | Type | Category | Bdlg # | CSD Estimated Signal Level |  | On File? | Total Sq Ftg | General Size |  | Address | Town | Lat_DMS | Long_DMS | X_coord | Y_coord | 10 site |  | 13 site |  | Percent RF Coverage |  | Building Loss dB
|  |  |  | 10 site | 13 site | [10 empty] | pass / fail | $ | pass / fail | $ | Test Transmitter | Control Channel | Test Transmitter | Control Channel | Absolute vaule differnce between Test tx and CC
B. Banneker Elementary School | School | C1 | 1 | -90 | -80 |  | 74000 | M | 1 story masonry | 27180 Point Lookout Rd. | Loveville | 38 19 42 | -76 40 36 | -76.6766 | 38.3308 | FAIL |  | PASS |  | 100% _100% | 91.4% | 18.7_23.2 | 13.9
B. Banneker Early Child Development | School | C1 | 2 | -90 | -80 |  | 37000 | S | 1 story - brick | 27110 Point lookout Rd | Loveville | 38 19 42 | -76 40 36 |  |  | FAIL |  | PASS |  | 100% | 87.7% | 25 | 14.3 | 10.7 | GPS 38-19.7 N x 076-40.6 W -- Adjacent to (300 yards + /-) and connected by covered walk to the above
Carver School |  |  | 1 |  |  | does not exist |  | M | 1 story masonry | 47382 Lincoln Ave | Lexington Park | 38 15 15 | -76 26 07 | -76.4354 | 38.2542 | [9 empty] | No longer a school -- Now partially a recreation center and partially a Sheriff's Station -- NO SURVEY -- See George Washington Carver Elementary
Charlotte Hall Veterans Home | A wing | C1 | 1 | -64 | -64 |  |  | LG | see notes | 29449 Charlotte Halll Rd. | Charlotte Hall | 38 28 44 | -76 46 41 | -76.7781 | 38.479 | PASS |  | PASS |  | 99.9% | 51.6% | 18.3 | 14.6 | 3.7 | (3) 1-story brick, (3) 3-story brick, (1) one "historic" house - use ?, (1) "historic" stone chapel -- Surveyed 9 buildings & checked BDA
| C Wing | C1 | 2 | -64 | -64 | [10 empty] | PASS |  | PASS |  | 84.7% | 35.5% | 37.7 | 18 | 19.7
| D Wing | C1 | 3 | -64 | -64 | [10 empty] | PASS |  | PASS |  | 83.7% | 17.2% | 42.5 | 21.4 | 21.1
| Core Building | C1 | 4 | -64 | -64 | [10 empty] | PASS |  | PASS |  | 96.9% | 24.2% | 26.3 | 21 | 5.3
Chesapeake Charter School | School | C1 | 1 | -85 | -85 |  | 25007 | M | 2 story metal skin | 20945 Great Mills Rd | Lexington Park | 38 14 33 | -76 29 32 | -76.4923 | 38.2426 | PASS |  | PASS |  | 100% | 95% | 4.3 | 5.1 | 0.8
Chesapeake Shores Nursing Home | Nursing Home | C1 | 1 | -68 | -68 |  |  | M | 1 story masonry | 21412 Great Mills Rd. | Lexington Park | 38 15 23 | -76 28 33 | -76.4758 | 38.2564 | PASS |  | PASS |  | 99% | 99% | 11.5 | 10.9 | 0.6
Chopticon High School | School | C1 | 1 | -77 | -77 |  | 216625 | LG | 2 story masonry | 25390 Colton Point Rd. | Morganza | 38 21 53 | -76 42 18 | -76.705 | 38.3648 | PASS |  | PASS |  | 99.7% | 86.5% | 21.2 | 16.3 | 4.9
College of Southern Md. | Bldg A | C1 | 1 | -74 | -75 |  |  | M | 2 story; masonry | 22950 Hollywood Rd. | Leonardtown | 38 17 55 | -76 38 04 | -76.6345 | 38.2987 | PASS |  | PASS |  | 99.9% | 99.8% | 18.8 | 6.6 | 12.2
| Bldg B | C1 | 2 | -74 | -75 | [10 empty] | PASS |  | PASS |  | 100% | 100% | 16.2 | 20.1 | 3.9
| Bldg C | C1 | 3 | -74 | -75 | [10 empty] | PASS |  | PASS |  | 100% | 99.9% | 11.1 | 9.8 | 1.3
Courthouse | Govt | C1 | 1 | -55 | -55 | jeff to send data |  | LG | 3 story brick | 41605 Court House Drive | Leonardtown | 38 17 24 | 76 38 12 |  |  | PASS |  | PASS | [6 empty] | GPS: 38-17.4 N x 076-38.2 W
Detention Center | Prison | C1 | 1 | -51 | -51 | Prison |  | LG | 1 & 2 story brick | 41880 Baldridge Street | Leonardtown | 38 18 12 | 76 37 42 |  |  | PASS |  | PASS |  | 98% | 100% | 35.9 | 27.9 | 8 | GPS: 38-18.2 N x 076-37.7 W
Dynard Elementary | School | C1 | 1 | -67 | -67 |  | 49200 | M to S | 1 story masonry | 23510 Bushwood Rd. | Bushwood | 38 18 53 | -76 45 33 | -76.7592 | 38.3148 | PASS |  | PASS |  | 100% | 63% | 16.2 | 7.2 | 9 | "H" shaped
Esperanza Middle | School | C1 | 1 | -73 | -73 |  | 115866 | M to L | 1 story masonry | 22790 Maple Rd. | California | 38 17 34 | -76 29 27 | -76.4908 | 38.2929 | FAIL |  | FAIL |  | 55% | 98% | 31.7 | 30.6 | 1.1
Evergreen Elementary | School | C1 | 1 | -91 | -87 |  | 76144 | M | 2 story brick | 43765 Evergreen Wy | California | 38 17 57 | 76 33 47 | -76.5645 | 38.3012 | FAIL |  | FAIL |  | 75% | 31% | 39.1 | 27.6 | 11.5 | GPS 38-17.953N 076-33.781W New school and road; not on maps, yet -- From SR235 & SR4, South on SR4 go 0.7 mile, Right onto Wildewood Pkwy go 3 miles, Right onto Evergreen Way
Fairlead Academy High School | School | C1 | 1 | -73 | -73 |  | 12672 | S | 1 story | 20833 Great Mills Road | Great Mills | 38 14 24 | 76 27 42 |  |  | PASS |  | PASS |  | 100% | 91% | 7.1 | 5.6 | 1.5 | (1) brick; (1) metal siding; (2) modular -- GPS: 38-14.4 N x 076-27.7 W
Forest Center Middle School | [5 empty] | later in list | [9 empty] | PASS |  | PASS | [5 empty] | 0 | Not a Middle School -- See Forest Tech Center
George Washington Carver Elementary | School | C1 | 1 | -84 | -84 |  | 61385 | LG | 1 story brick | 46155 Carver School Blvd | Lexington Park | 38 15 0.3 | 76 28 48.3 |  |  | PASS |  | PASS |  | 97% | 99% | 11.1 | 13.1 | 2 | New school and road; not on maps, yet -- From Three Notch Rd, 1.8 miles SW on Great Mills Rd, Left onto Carver School Blvd to the end -- GPS 38-15.005 N x 076- 28.805 W
Great Mills High School | School | C1 | 1 | -81 | -82 |  | 216625 | LG | 2 story masonry | 21130 Great Mills Rd. | Lexington Park | 38 14 50 | -76 29 22 | -76.4896 | 38.2471 | PASS |  | PASS |  | 84% | 96% | 25.6 | 11.8 | 13.8
Green Holly School | School | C1 | 1 | -76 | -76 |  | 46450 | LG | 1 story; masonry | 46060 Millstone Landing Rd. | California | 38 17 41 | -76 28 54 | -76.4816 | 38.2947 | PASS |  | PASS |  | 100% | 100% | 23.1 | 8 | 15.1
| School | C1 | 2 |  |  |  | 57925
Greenview Knolls Elementary | School | C1 | 1 | -72 | -72 |  | 54239 | M | 1 story masonry | 45711 Military Ln. | Great Mills | 38 16 49 | 76 29 35 | -76.495 | 38.2804 | PASS |  | PASS |  | 100% | 100% | 20.9 | 15.6 | 5.3 | GPS 38-16.814N 076-29.595W
Higher Education Center | School | C1 | 1 | -91 | -86 |  |  | M | 2 sections; masonry | 44219 Airport Rd | California | 38 18 49 | -76 32 43 | -76.5452 | 38.3137 | FAIL |  | FAIL |  | 100% | 57% | 23.4 | 15.2 | 8.2 | 1 story, brick, 2 buildings
Hollywood Elementary | School | C1 | 1 | -82 | -76 |  | 57565 | M to L | masonry 1 story | 44345 Joy Chapel Rd. | Hollywood | 38 20 26 | -76 32 24 | -76.54 | 38.3406 | PASS |  | PASS |  | 100% | 55% | 20 | 13.3 | 6.7 | Also, at least one modular
Kings Christian Academy | School | C1 | 1 | -72 | -72 |  |  | S | 1 story brick | 20738 Point Lookout Rd; near RT5 and RT 249 | Callaway | 38 14 30 | 76 31 00 |  |  | PASS |  | PASS |  | 100% | 93% | 13.5 | 15.7 | 2.2 | Also, 2 modular buildings -- GPS: 38-14.5 N x 076-31.0 W
Leonardtown Elementary | School | C1 | 1 | -69 | -70 |  | 67847 | M | 1 story masonry | 22885 Duke St. | Leonardtown | 38 17 48 | -76 38 22 | -76.6381 | 38.2969 | PASS |  | PASS |  | 99.8%_100% | 99.7% | 33.9_20.6 | 7.8
Leonardtown High School | School | C1 | 1 | -73 | -65 |  | 223727 | LG | 2 story masonry | 23995 Point Lookout Rd. | Leonardtown | 38 16 11 | -76 36 40 | -76.6093 | 38.2714 | PASS |  | PASS |  | 96.7%_95.8% | 86.9% | 30.8_30.3 | 20.3 |  | Also, Forest Tech Center is adlacent
Leonardtown Middle | School | C1 | 1 | -75 | -60 |  | 106677 | LG | 1 story masonry | 24015 Point Lookout Rd. | Leonardtown | 38 16 26 | -76 36 44 | -76.6096 | 38.2719 | PASS |  | PASS |  | 100%_99.9%_99.6%_99.6% | 91.6% | 36.1_35.5_32.8_27.6 | 16.7
Lettie Marshall Dent Elem | School | C1 | 1 | -61 | -61 |  | 57820 | M | 1 story masonry | 37840 New Market Turner Rd. | Mechanicsville | 38 28 24 | -76 46 06 | -76.7683 | 38.4733 | PASS |  | PASS |  | 99.8% | 46.5% | 23.6 | 17.8 | 5.8
Lexington Park Elementary | School | C1 | 1 | -85 | -85 |  | 56000 | S | 1 story masonry | 46763 South Shangri La Dr. | Lexington Park | 38 15 39 | -76 27 28 | -76.4577 | 38.2608 | FAIL |  | FAIL |  | 96% | 96% | 16 | 13.1 | 2.9
Loville Elementary | School |  |  |  |  | does not exist | 23527 | [8 empty] | PASS |  | PASS | [5 empty] | 0 | Old name for Benjamin Banneker
Margaret Brent Middle | School | C1 | 1 | -74 | -74 |  | 131354 | LG | masonry 1 story | 29675 Point Lookout Rd. | Helen | 38 22 45 | -76 42 47 | -76.713 | 38.3791 | PASS |  | PASS |  | 99.6% | 62.1% | 30.5 | 19.5 | 11
Mechanicsville Elementary | School | C1 | 1 | -72 | -70 |  | 40095 | M | 1 story masonry | 28585 Three Notch Rd. | Mechanicsville | 38 27 10 | -76 45 09 | -76.7525 | 38.4528 | PASS |  | PASS |  | 100% | 94.5% | 15.3 | 7.6 | 7.7 | Also, 4 modular buildings
Oakville Elementary | School | C1 | 1 | -60 | -60 |  | 48072 | M to L | 1 story masonry | 26410 Three Notch Rd | Mechanicsville | 38 23 37 | -76 38 55 | -76.6486 | 38.3936 | PASS |  | PASS |  | 100% | 88.1% | 16.6 | 13.2 | 3.4 | Also, 2 modular buildings
Park Hall Elementary | School | C1 | 1 | -76 | -76 |  | 58419 | M to L | 1 story masonry | 20343 Hermanville Rd. | Park Hall | 38 13 34 | -76 26 59 | -76.4498 | 38.2261 | PASS |  | PASS |  | 99.5% | 92.5% | 12.6 | 11.5 | 1.1
Phillip J. Bean Medical Center | Hospital | C1 | 1 | -89 | -80 |  |  | LG | 2 story masonry | 24035 Three Notch Rd. | Hollywood | 38 19 41 | -76 33 10 | -76.5526 | 38.3281 | FAIL |  | FAIL |  | 99% | 52% | 29.7 | 24.4 | 5.3
Piney Point Elementary | School | C1 | 1 | -86 | -86 |  | 57794 | M | 1 story masonry | 44550 Tall Timbers Rd | Tall Timbers | 38 09 52 | -76 32 08 | -76.5354 | 38.1643 | FAIL |  | FAIL |  | 89% | 73% | 14.2 | 14.1 | 0.1
Ridge Elementary | School | C1 | 1 | -77 | -77 |  | 32537 | S | 1 story masonry | 49430 Airedale Rd. | Ridge | 38 06 36 | -76 22 02 | -76.3672 | 38.1101 | PASS |  | PASS |  | 100% | 17.3% | 9.9 | 11.9 | 2 | Also, 2 modular buildings
Ryken High School Campus | Paschal Hall | C1 | 1 | -73 | -73 |  |  | Very LG | 1 & 2 story brick | 22600 Camp Calvert Road | Leonardtown | 38-18-07 | 76-31-16 |  |  | PASS |  | PASS |  | 100% | 99.8% | 18.8 | 10.1 | 8.7 | I counted 5 buildings
| Romuald Hall | C1 | 1 | -73 | -73 | [10 empty] | PASS |  | PASS |  | 100% | 98.7% | 15.3 | 14.6 | 0.7
| Rupert Hall | C1 | 1 | -73 | -73 | [10 empty] | PASS |  | PASS |  | 98.4% | 97.4% | 26.4 | 18.6 | 7.8
Spring Ridge Middle | School | C1 | 1 | -78 | -77 |  | 104750 | M | 1 story masonry | 19856 Three Notch Rd. | Lexington Park | 38 12 45 | -76 24 11 | -76.403 | 38.2124 | PASS |  | PASS |  | 99.5% | 52.2% | 16.1 | 18.5 | 2.4
St. Mary's College Of MD. | Admissions | C1 | 1 | -80 | -80 |  |  | HUGE | see notes | 17060 Point Lookout Rd. | St. Mary's City | 38 11 25 | -76 25 51 | -76.4309 | 38.1902 | PASS |  | PASS |  | 56.9% | 83.9% | 12.2 | 11.5 | 0.7 | 40+ buildings; 1, 2, and 3 story brick; Campus covers 200+ acres
| AthlRec Ctr | C1 | 2 | -80 | -80 | [10 empty] | PASS |  | PASS |  | 67.7% | 83% | 12 | 12.1 | 0.1
| Calvert Hall | C1 | 3 | -80 | -80 | [10 empty] | PASS |  | PASS |  | 99.3% | 91.2% | 10.7 | 10.4 | 0.3
| Campus Center | C1 | 4 | -80 | -80 | [10 empty] | PASS |  | PASS |  | 85.2% | 48.8% | 22.6 | 15.7 | 6.9
| Maint Build | C1 | 5 | -80 | -80 | [10 empty] | PASS |  | PASS |  | 93.5% | 98.3% | 8.1 | 5.2 | 2.9
| Montgomery Hall | C1 | 6 | -80 | -80 | [10 empty] | PASS |  | PASS |  | 77.6% | 65% | 16.4 | 16.1 | 0.3
| Prince George Hall | C1 | 7 | -80 | -80 | [10 empty] | PASS |  | PASS |  | 99.4% | 93.3% | 11.8 | 10.6 | 1.2
| River Center | C1 | 8 | -80 | -80 | [10 empty] | PASS |  | PASS |  | 78.1% | 75.1% | 16.4 | 15 | 1.4
| Schaefer Hall |  |  | -80 | -80 | [10 empty] | PASS |  | PASS |  | 64.4% | 59.6% | 17.2 | 16.2 | 1
St. Mary's Hospital | Hospital | C1 | 1 | -69 | -69 |  |  | LG | basement + 2 stories | 25500 Point Lookout Rd. | Leonardtown | 38 17 57 | -76 38 25 | -76.6402 | 38.2992 | PASS |  | PASS |  | 94%_96% | 97% | 30.6_33.8 | 24.6 |  | I counted 3 stories above ground -- Brick
St. Mary's Nursing Center | Nursing Home | C1 | 1 | -75 | -75 |  |  | LG | 4 story masonry | 21585 Peabody St. | Leonardtown | 38 17 56 | -76 38 13 | -76.6371 | 38.299 | PASS |  | PASS |  | 100%_100% | 99.9% | 19.3_17 | 12.8
Forest Tech Center | School | C1 | 1 | -76 | -76 |  |  | LG | 1 story masonry | 24005 Point Lookout Rd | Leonardtown | 38-16-18 | 76-36-39 |  |  | PASS |  | PASS |  | 100%_99.9%_99.8%_99.9% | 94.4% | 30.5_39.1_35.2_24.9 | 10.4 |  | located beside Leonardtown High School
Town Creek Elementary | School | C1 | 1 | -80 | -80 |  | 35498 | M | 1 story masonry | 45805 Dent Dr. | Lexington Park | 38 18 12 | -76 29 25 | -76.4902 | 38.3034 | PASS |  | PASS |  | 100% | 97% | 24.1 | 12 | 12.1 | Also, modulars
White Marsh Elementary | School | C1 | 1 | -72 | -72 |  | 31315 | S | 1 story masonry | 29090 Thompson Corner Rd. | Mechanicsville | 38 28 02 | -76 46 39 | -76.7774 | 38.4672 | PASS |  | PASS |  | 100% | 59% | 23.7 | 11.9 | 11.8 | Also, 2 modular buildings
CRITICAL TWO BUILDINGS
Building_Name | Type | Category | Bdlg # |  |  |  | Total Sq Ftg | General Size |  | Address | Town | Lat_DMS | Long_DMS | X_coord | Y_coord
LaQuinta Inn & Suites | Hotel | C2 | 1 | -71 | -71 |  |  | LG | 3 story; masonry | 22769 Three Notch Rd. | California | 38 17 34 | -76 29 50 | -76.4972 | 38.2929 | PASS |  | PASS |  | 100% | 100% | 13.7 | 11.3 | 2.4
Sleep Inn & Suites | Hotel | C2 | 1 | -74 | -73 |  |  | LG | 3 story; masonry | 23248 Three Notch Rd. | California | 38 18 42 | 76 32 00 | -76.5249 | 38.3059 | PASS |  | PASS |  | 100% | 97% | 11.2 | 9.5 | 1.7 | Given coordinates are more than 6/10 mile from actual location; GPS: 38-18.7 N x 076-32.0 W
Super 8 | Hotel | C2 | 1 | -75 | -75 |  |  | M | 3 story; stucco | 22801 Three Notch Rd. | California | 38 17 37 | -76 29 56 | -76.4989 | 38.2936 | PASS |  | PASS |  | 100% | 100% | 11.2 | 4.3 | 6.9
Country Inn & Suites | Hotel | C2 | 1 | -73 | -72 |  |  | LG | 4 story masonary | 44941 Worth Ave. | California | 38 18 08 | -76 31 14 | -76.5206 | 38.3021 | PASS |  | PASS |  | 100% | 93.3% | 16.8 | 6.4 | 10.4
Wal-Mart | Commercial | C2 | 1 | -75 | -75 |  |  | LG | 1 story masonary | 45485 Miramar Wy | California | 38 17 38 | -76 30 08 | -76.5023 | 38.2939 | FAIL |  | FAIL |  | 100% | 95% | 26.1 | 25.3 | 0.8
Best Buy | Commercial | C2 | 1 | -75 | -75 |  |  | M | 1 story masonary | 45235 Worth Av | California | 38 17 49 | -76 30 36 | -76.51 | 38.297 | PASS |  | PASS |  | 100% | 100% | 10.4 | 18.5 | 8.1
Petco1 | Commercial | C2 | 1 | -77 | -77 |  |  | M | 1 story masonary | 45205 Worth Av | California | 38 17 53 | -76 30 42 | -76.5116 | 38.2979 | FAIL |  | FAIL |  | 100% | 100% | 7.2 | 29.2 | 22
Target | Commercial | C2 | 1 | -78 | -78 |  |  | LG | 1 story masonary | 45155 First Colony Wy | California | 38 17 51 | -76 30 49 | -76.5135 | 38.2974 | PASS |  | PASS |  | 100% | 94% | 24.1 | 18.5 | 5.6
Lowes | Commercial | C2 | 1 | -80 | -80 |  |  | LG | 1 story masonary | 45075 Worth Ave | California | 38 18 01 | -76 30 55 | -76.5152 | 38.3002 | FAIL |  | FAIL |  | 100% | 87% | 26 | 30.1 | 4.1
BJ's Wholesale | Commercial | C2 | 1 | -73 | -73 |  |  | LG | 1 story masonary | 44950 Worth Ave | California | 38 18 09 | -76 31 14 | -76.5204 | 38.3025 | FAIL |  | FAIL |  | 100% | 90% | 23 | 28.7 | 5.7
JC Penny | Commercial | C2 | 1 | -74 | -74 |  |  | M | 1 story masonary | 23415 Three Notch Rd. | California | 38 18 38 | -76 31 58 | -76.5327 | 38.3105 | PASS |  | PASS |  | 100% | 44% | 17 | 17.2 | 0.2
Belk | Commercial | C2 | 1 | -74 | -74 |  | same as above | M | 1 story masonary | 23415 Three Notch Rd. | California | 38 18 38 | -76 31 58 | -76.5327 | 38.3105 | PASS |  | PASS |  | 100% | 67% | 20.3 | 16.8 | 3.5
ONE BUILDING ONLY | Commercial | C2 | 2
K-Mart | Commercial | C2 | 1 | -75 | -75 |  |  | LG | 1 story masonary | 45315 Alton Ln. | California | 38 17 45 | -76 30 28 | -76.5077 | 38.2958 | FAIL |  | FAIL |  | 100% | 95% | 25 | 24.8 | 0.2
Executive Inn & Suites | Hotel | C2 | 1 | -71 | -71 |  |  | M | 3 story masonary | 41655 Park Ave | Leonardtown | 38 17 25 | -76 38 07 | -76.6352 | 38.2903 | PASS |  | PASS |  | 100% | 99.9% | 1.6 | 1.8 | 0.2
Cedar Lane Apts | Residential | C1 | 3 | -70 | -70 |  |  | LG | 4 story masonary | 22680 Cedar Ln. | Leonardtown | 38 17 25 | -76 37 28 | -76.6246 | 38.2904 | PASS |  | PASS |  | 94.8% | 99.2% | 14 | 10.8 | 3.2 | 3 or 4 buildings
Days Inn | Hotel | C2 | 1 |  |  | no survey |  | LG | 3-4 story | 21847 Three Notch Rd. | Lexington Park | 38 16 01 | -76 27 20 | -76.4557 | 38.2669 | [9 empty] | I counted 7 buildings - All are 2 story - Concrete (or stucco) No interior hallways - All rooms open to the outside - NO SURVEY
Fairfield Inn | Hotel | C2 | 1 | -76 | -76 |  |  | M | 4 story masonary | 22119 Three Notch Rd. | Lexington Park | 38 16 27 | 76 27 48 | -76.4627 | 38.2739 | PASS |  | PASS |  | 99% | 97% | 10.5 | 9.6 | 0.9 | GPS 38-16.454N 076-27.814W
Extended Stay America | Hotel | C2 | 1 | -64 | -64 |  |  | M | 3 story masonry | 46565 Expedition Dr. | Lexington Park | 38 16 38 | 76 27 51 | -76.4664 | 38.2799 | PASS |  | PASS |  | 100% | 99% | 12.8 | 9.7 | 3.1 | GPS 38-16.687N 076-27.849W
Hampton Inn | Hotel | C2 | 1 | -74 | -74 |  |  | M | 5 story concrete | 22211 Three Notch Rd | Lexington Park | 38 16 38 | 76 27 57 | -76.4635 | 38.275 | PASS |  | PASS |  | 100% | 99% | 13.4 | 4.9 | 8.5 | GPS 38-16.633 076-27.946
TownPlace Suites | Hotel | C2 | 1 | -72 | -72 |  |  | M | 3 story masonry | 22520 Three Notch Rd. | Lexington Park | 38 17 13 | 76 28 33 | -76.4772 | 38.2864 | PASS |  | PASS |  | 100% | 100% | 18.1 | 14.5 | 3.6 | GPS 38-17.227N 076-28.560W
AMC Theatres | Theatre | C2 | 1 | -82 | -82 |  |  | S | 1 story | 21882 FDR Blvd | Lexington Park | 38 16 09 | -76 27 33 | -76.459 | 38.2693 | PASS |  | PASS |  | 100% | 98% | 10.2 | 16.1 | 5.9 | Concrete block
New Town Village | Residential | C1 | 1 |  |  | no survey |  | S | 3 story | 22810 Dorsey St | Leonardtown | [13 empty] | GPS 38-17.680N 076-38.390W --- Frame construction with plastic siding -- THREE ATEMPTS TO GAIN ENTRY - NO SURVEY - Good signal inside nearby brick buildings
Paul Hall Trng & Conf Center | Residential | C1 | 1 | -85 | -85 |  |  | M | 6 story masonry | 17270 Piney Point Rd | Piney Point | 38 8 41 | 76 30 16.5 |  |  | PASS |  | PASS |  | 100% | 88% | 18.5 | 9.6 | 8.9 | GPS 38-08.678N 076-30.275W
***Lexington Park Senior Center | SEE NOTE |  |  |  |  | see line 33 |  |  |  | 21907 Pegg Rd | Lexington Park | [13 empty] | ***NO FACILITY WITH THIS NAME -- NOTHING LOCATED WHERE 21907 PEGG RD WOULD BE -- SEE LEXINGTON PARK ACTIVE ADULT COMMUNITY
L-3 Titan Group Corp | Commercial | C2 | 1 | -75 | -75 |  |  | M |  | 22290 Exploration Dr | Lexington Park | 38 16 47 | 76 28 6 |  |  | PASS |  | PASS |  | 99% | 99% | 2.8 | 7.2 | 4.4 | GPS 38-16.785N 076-28.094W
River Bay Town Homes | Residential | C1 | Many |  |  | no survey |  | Community | See Notes | 48100 Bayswood Rd | Lexington Park | [13 empty] | GPS 38-15.238N 076-24.880W (Near center of community) -- Apt style and single family style -- frame & plastic siding (some single family have brick fronts -- Survey done "In-Street"
Lexington Park Active Adult Community | Residential | C1 | 1 | -76 | -76 |  |  | M | 3 story brick | 21895 Pegg Rd | Lexington Park | 38 16 11 | 76 28 16 |  |  | PASS |  | PASS |  | 99% | 100% | 14.1 | 2.1 | 12 | GPS 38-16.177N 076-28.267W --
Note 1 = see r5 - Petco may also pass - high outside signal level but difference in building loss values between cc and test tx. | [22 empty] | AVG difference test tx and cc | 5.3958
[23 empty] | Std Deviation | 5.1457

## Notes
Column E and F
CSD Estimated Signal Level - RCC propagation program Comsite Design used to predict signal levels at building locations. TSB 88 inferred noise and faded signal levels used to predict DAQ 3.4 voice quality.
Column Q thru T
Predicted ITAC Coverage (-97 dBm) - CSD predicted signal level minus measured building loss has to be greater than -97 dBm (TSB-88 DAQ 3.4 Signal level) to pass.
Column U and V
Tested for P25 (-105 dBm) - test results copied from individual building workbooks indicating the % of grids that had > -105 dBm signal level using existing control channel.
-105 dBm signal level is TSB 88 DAQ 3.4 portable at head level.
Test transmitter column is for informational only - details can be found in each buildings workbook.
Column W and X
Building Loss dB -test results copied from individual building workbooks indicating the average loss of the building from both the existing control channel and a test transmitter parked near the building.
Column Y
Correlation calculatons between the existing control channel and test transmitter data.